## Summary
S.No. | Description | Amount, Nrs | Remarks
1 | Electrical and allied works
2 | Sanitary and plumbing works
3 | Fire Fighting System
4 | HVAC System
5 | Fire Alarm System
6 | CCTV System
Sub Total, Nrs.
VAT@13%
Total With VAT, Nrs.

## MEP BOQ
S.No. | Description of Item | Unit | Qty. | Rate in word (N Rs.) |  | Amount (NRs.) | Remark
|  |  |  | In Figure | In word
ELECTRICAL AND ALLIED WORKS
A | CIRCUIT CUM POINT WIRING (SUPPLY, INSTALLATION, TESTING AND COMMISSIONING)
1 | Point wiring for Standard Room
1.1 | Wiring for the following light points with 2.5 sq.mm and power outlet points with 4 sq.mm PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires of approved make in concealed or surface mounted 25 mm dia 16 gauge GI conduits including supply, fixing of modular switches and socket outlet with boxes including earthing of third pin of the socket outlet with 4 sq.mm and light points with 2.5 sq.mm PVC insulated copper conductor stranded flexible wire. Each type of suite shall contain the following point through the master switch as per requirement. (All socket out lets shall be Universal type)
i. | 6 amps socket outlet - 10 Nos.
ii. | 16 amps socket outlet - 4 Nos.
iii. | Shaver socket outlet - 1 No.
iv. | FCU point - 1 No.
v. | Light points - 16 Nos.
vi. | DND/ Make my room/ Bell Push set up with suitable icon - 1 No.
vii. | Anti Fog Pad for Mirror - 1 No.
viii | 3 Gang way media hub (with connectivity kit) - 1 No.
ix. | Data Point
x. | Telephone Point
1.2 | Unloading, forwarding, shifting from stores to site, storing, handling, installation and commissioning of following items including all accessories complete as required.
i. | Down Lighter- 10 W - 4 Nos.
ii. | Twin Adjustable LED light 18 W - 6 Nos.
iii. | Night lamp - 1 No.
iv. | LED Strip Cove lights - 15 RM
v. | Wall Light - 1 No.
vi. | Chandelier - 1 No.
vii. | Pendant Light, Suspended-1 No.
| Room described as above | Nos. | 66
1 | Wiring for the following light points with 2.5/1.5 sq.mm (2.5 sqmm upto primary point & 1.5 sqmm from primary to secondry) PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires of approved make in 25 mm dia. 16 gauge MS conduit as per IS 9537 concealed or surface mounted including providing and fixing of 6 amps single pole rocker operated flush mounted switch of approved quality colour make & design mounted on 1.6 mm thick GI box and earthing of fixtures and the outlet box with 2.5/1.5 sq.mm PVC insulated copper conductor stranded flexible "ZHFR" wire. (1st point with 2.5 sqmm & looping shall be with 1.5 Sqmm)
1.1 | Primary point controlled by one 6 amps switch. Wiring for primary point shall be done in 25 mm dia. conduit (Average Length shall be 8 Mtrs.) | Pts. | 220
1.2 | Same as item no. 1.1) above but Secondary point (Controllling switch is included in item no. 1.1) Wiring for secondary point shall be done in 19 mm dia. conduit. (Average Length shall be 3 Mtrs.) | Pts. | 450
2 | Wiring for 250 volts single phase and neutral 6 amps switched socket outlet with 2.5/1.5 sq.mm (2.5 sqmm upto primary point & 1.5 sqmm from primary to secondry) PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in concealed or surface mounted 25mm dia. 6 gauge MS conduit as per IS 9537 including providing and fixing of 6 amps 3 pin switch socket outlet of aprpoved make and design in 1.6 mm thick GI box with grid plate and earthing of third pin of the socket with 2.5 /1.5 Sq. mm PVC insulated copper conductor stranded flexible "ZHFR" wire (maximum eight no. of switches socket shall be connected on one circuit) (1st point with 2.5 sqmm & looping shall be with 1.5 Sqmm)
2.1 | Primary Point controlled by one 6 amp switch. | Point | 165
2.2 | Same as item No. 3 above, but Secondary point. | Point | 450
3 | Wiring for 250 volts single phase and neutral 6/16 amps switched socket outlet with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in concealed or surface mounted 25 mm dia. 16 gauge MS conduit as per IS 9537 including providing and fixing of 16 amps 3 pin switched sockets of approved make and design in 1.6 mm thick GI box with grid plates and earthing the third pin of each socket outlet with 4 Sq mm PVC insulated copper conductor stranded flexible "ZHFR" wire (2 nos. socket outlet shall be looped on one circuit). | Point | 350
4 | Wiring for light point as in item No. A-1 above but controlled by SPMCB provided in the DB. (Cost of MCB not to be included here).(1st point with 2.5 sqmm & looping shall be with 1.5 Sqmm)
4.1 | MCB controlled Primary point (from dimmer/ MCB to first light point) | Pts. | 50
4.2 | MCB controlled Secondary point (from point to point of same circuit) | Pts. | 250
5 | Wiring for 250 volts single phase and neutral 16 amps polycarbonate industrial 3 pin (IP 65/66)socket outlet with 16 amps double pole MCB in a poly carbonate enclosure of approved size and design with interlocked rotary switch 4 sq.,mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in surface / recessed 25 mm dia. 16 gauge MS conduit as per IS 9537 , including providing and fixing of 16 amps socket in poly carbonate enclosure and earthing of third pin of the socket and with 4 sq.mm PVC insulated copper conductor stranded flexible "ZHFR" wire. | Point | 30
6 | Wiring for 250 volts single phase and neutral 20 amps polycarbonate industrial 3 pin (IP 65/66)socket outlet with 20 amps double pole MCB in a poly carbonate enclosure of approved size and design with interlocked rotary switch 4 sq.,mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in surface / recessed 25 mm dia. 16 gauge MS conduit as per IS 9537 , including providing and fixing of 20 amps socket in poly carbonate enclosure and earthing of third pin of the socket and with 4 sq.mm PVC insulated copper conductor stranded flexible "ZHFR" wire. | Point | 10
7 | Wiring for 250 volts single phase and neutral 32 amps polycarbonate industrial 3 pin (IP 65/66)socket outlet with 32 amps double pole MCB in a poly carbonate enclosure of approved size and design with interlocked rotary switch 6 sq.,mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in surface / recessed 25mm dia. 16 gauge MS conduit as per IS 9537, including providing and fixing of 32 amps socket with rotary switch in poly carbonate enclosure and earthing of third pin of the socket and with 6 sq.mm PVC insulated copper conductor stranded flexible "ZHFR" wire. | Point | 8
8 | Wiring for 250 volts single phase and neutral 63 amps polycarbonate industrial 3 pin (IP 65/66)socket outlet with 63 amps double pole MCB in a poly carbonate enclosure of approved size and design with interlocked rotary switch 6 sq.,mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in surface / recessed 25mm dia. 16 gauge MS conduit as per IS 9537, including providing and fixing of 63 amps socket with rotary switch in poly carbonate enclosure and earthing of third pin of the socket and with 6 sq.mm PVC insulated copper conductor stranded flexible "ZHFR" wire. | Point | 8
9 | Wiring for 250 volts single phase and neutral 40 amps polycarbonate industrial 3 pin (IP 65/66)socket outlet with 63 amps double pole MCB in a poly carbonate enclosure of approved size and design with interlocked rotary switch 6 sq.,mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in surface / recessed 25mm dia. 16 gauge MS conduit as per IS 9537, including providing and fixing of 40 amps socket with rotary switch in poly carbonate enclosure and earthing of third pin of the socket and with 6 sq.mm PVC insulated copper conductor stranded flexible "ZHFR" wire. | Point | 10
LIFT SHAFTS
10 | Wiring for following 250 volts single phase and neutral 16 amps switched socket outlet for lift shafts with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires in surface / recessed 25 mm dia 16 gauge MS conduit including providing and fixing of 16 amps 3 pin switched socket of approved make and design in 2 mm thick GI boxes with grid plates and earthing of third pin of socket outlet and GI box with 2.5 sq.mm PVC insulated copper conductor stranded flexible ZHFR wire.
10.1 | 4 Nos. 16 amps switched socket outlet on one circuit | Sets | 10
10.2 | 6 Nos. 16 amps switched socket outlet on one circuit | Sets | 10
11 | Supply, installation & wiring of 230 V bulk head lamp with on/off switch for Lift shafts with 2.5 sq.mm PVC insulated copper conductor 1100V grade stranded flexible "ZHFR" wires in 25 mm dia 16 gauge MS conduit including providing and fixing of 6A switch with 2.5 sq.mm. PVC insulated "ZHFR" copper conductor stranded flexible earth wire.
11.1 | 4 Nos. Bulk head lamps with switch on one circuit | Sets | RO
11.2 | 8 Nos. Bulk head lamps with switch on one circuit | Sets | 10
12 | Providing and fixing of following PVC insulated copper conductor 1100 volt grade stranded flexible "ZHFR" wire in existing 25mm dia. 16 gauge MS conduits making connections where ever required to complete the installation.
12.1 | 3 Nos. 2.5 sq.m PVC insulated copper conductor 1100 volts grade stranded flexible "ZHFR" wires | RM | 100
12.2 | 3 Nos. 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded "ZHFR" wires | RM | 100
13 | Supply and fixing of 25mm dia. 2mm thick embeded PVC conduits of following sizes including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab, cutting chasis and making good including all fixing hardware. (Electrical and LV system).
13.1 | 20 mm dia 2mm thick PVC | RM | R/O
13.2 | 25 mm dia 2mm thick PVC | RM | 3000
13.3 | 32 mm dia 2mm thick PVC | RM | 100
13.4 | 50 mm dia 2mm thick PVC | RM | R/O
TOTAL CARRIED TO SUMMARY
B | CABLES, MAINS, SUB MAINS AND CABLE TRAYS
1 | Supplying & laying of following 1100 volt grade XLPE insulated PVC sheathed aluminium conductor armoured cables as per specification in existing trenches, cable trays, ducts, over bed of sand, clamped to wall with suitable clamps including, saddles fixing bolts, connecting testing and commissioning.
1.1 | 3.1/2 core 300 sq. mm | RM | 350
1.2 | 3.1/2 core 240 sq. mm. | RM | 0
1.3 | 3.1/2 core 185 sq. mm. | RM | 0
1.4 | 3.1/2 core 150 sq. mm | RM | 100
1.5 | 3.1/2 core 120 sq.mm | RM | 0
1.6 | 3.1/2 core 95 sq. mm | RM | 0
1.7 | 3.1/2 core 70 sq. mm | RM | 330
1.8 | 3.1/2 core 50 sq. mm | RM | 450
1.9 | 3.1/2 core 35 sq. mm | RM | 425
1.1 | 3.1/2 core 25 sq. mm | RM | 150
1.11 | 4 core 35 sq. mm | RM | 200
1.12 | 4 core 25 sq. mm | RM | 120
2 | Supplying & laying of following 1100 volt grade XLPE insulated PVC sheathed copper conductor armoured cables as per specification in existing trenches, cable trays, ducts, over bed of sand, clamped to wall with suitable clamps including, saddles fixing bolts, connecting testing and commissioning.
2.1 | 4 core 16 sq.mm | RM | 100
2.2 | 4 core 10 sq. mm. | RM | 250
2.3 | 4 core 6 sq.mm | RM | 100
2.4 | 4 core 4 sq.mm | RM | 150
2.5 | 3 core 6 sq.mm | RM | 150
2.6 | 3 core 10 sq.mm | RM | 1650
2.7 | 3 core 16 sq.mm | RM | 250
2.8 | 3 core 4 sq.mm | RM | R/O
2.9 | 2 core 2.5 sq.mm control cable | RM | 50
2.1 | 4 core 2.5 sq.mm control cable | RM | 50
2.11 | 7 core 2.5 sq.mm control cable | RM | 50
2.12 | 12 core 2.5 sq.mm control cable | RM | 50
3 | Cable end termination of the following XLPE insulated PVC sheathed aluminium/ copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing.
3.1 | 3.1/2 core 300 sq. mm. Aluminium Cable | Nos. | 8
3.2 | 3.1/2 core 240 sq. mm. Aluminium Cable | Nos. | 0
3.3 | 3.1/2 core 185 sq. mm. Aluminium Cable | Nos. | 0
3.4 | 3.1/2 core 150 sq. mm. Aluminium Cable | Nos. | 4
3.5 | 3.1/2 core 120 sq. mm. Aluminium Cable | Nos. | 0
3.6 | 3.1/2 core 95 sq. mm. Aluminium Cable | Nos. | 0
3.7 | 3.1/2 core 70 sq. mm. Aluminium Cable | Nos. | 12
3.8 | 3.1/2 core 50 sq. mm. Aluminium Cable | Nos. | 0
3.9 | 3.1/2 core 35 sq. mm Aluminium Cable | Nos. | 16
3.1 | 3.1/2 core 25 sq. mm Aluminium Cable | Nos. | 10
3.11 | 4 core 16 sq. mm Copper Cable | Nos. | 10
3.12 | 4 core 10 sq. mm Copper Cable | Nos. | 16
3.13 | 4 core 6 sq. mm Copper Cable | Nos. | 18
3.14 | 4 core 4 sq. mm Copper Cable | Nos. | 20
3.15 | 3 core 16 sq.mm Copper Cable | Nos. | 10
3.16 | 3 core 10 sq. mm Copper Cable | Nos. | 160
3.17 | 3 core 6 sq. mm Copper Cable | Nos. | 6
3.18 | 3 core 4 sq.mm Copper Cable | Nos. | 6
4 | Supply and fixing GI ladder type cable trays, with radial bends, supports of the following sizes as per specification.
4.1 | 1200 mm wide
Runners 25 x 100 x 25 x 3 mm
Rungs 20 x 40 x 20 x 3 mm 250 mm C/C
| Suspenders 2 Nos. 40 x 405 x 5 mm GI angle 1500 mm C/C | RM | 50
4.2 | 900 mm wide
Runners 25 x 100 x 25 x 3 mm
Rungs 20 x 40 x 20 x 3 mm 250 mm C/C
| Suspenders 2 Nos. 40 x 40 x 5 mm GI angle 1500 mm C/C | RM | 75
4.3 | 750 mm wide
Runners 20 x 75 x 20 x 2.5 mm
Rungs 20 x 30 x 20 x 2.5 mm 250 mm C/C
| Suspenders 2 Nos. 32 x 32 x 5 mm GI angle 1800 mm C/C | RM | 65
5 | Supply and fixing of perforated type pregalvanized GI cable trays of the following sizes including providing 2 Nos. 25 x 25 x 4 mm GI angle suspenders at 1800 mm C/C as per specifications.
5.1 | 600 mm x 40 x 40 x 1.6 mm thick | RM | 95
5.2 | 450 mm x 40 x 40 x 1.6 mm thick | RM | 100
5.3 | 300 mm x 40 x 40 x 1.6 mm thick | RM | 200
5.4 | 150 mm x 25 x 25 x 1.6 mm thick | RM | 295
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
C | DISTRIBUTION BOARDS
Design, fabrication, assembling, supply, installation, testing and commissioning of Main LT panel, Main Distribution Panels, Sub Distribution panels and Final Distribution panels suitable for 415 V, 3 phase, 50 Hz, 4 wire power supply system.
Panels shall be fabricated out of 2 mm thick CRCA sheet steel in cubical formation, compartmentalized in Form 3b Construction, floor mounted, free standing and shall be dust and vermin proof. 3 mm thick cable gland plate, shall be provided both at the top and the bottom of the panel.
Final distribution panels shall be fabricated out of 1.6 mm thick CRCA sheet steel and shall be wall mounted. All large panels shall be provided with lifting hooks. Distribution panels shall be fabricated in accordance with the specifications.
1 | Main LT Panel:
A. | Incoming MCCB `A’
(For DG supply)
630 amps 4 pole motorized moulded case circuit breaker with built in microprocessor based release unit for protection as per specification and with following accessories :
i. | Multifunctional meter (conzerve - EM3360 or equivalent) of accuracy class-I, with 3 nos. 630/ 5 amps 5 VA CTs to measure.
1 Set
ii. | Phase indicating light through 415/ √3 : 110V/ √3 PT, Primary/ Secondary of PT's shall be protected by 2 amps MCB’s.
1 Set
iii. | Breaker ON/ OFF/ TRIP indicating lights with control MCB’s
1 Set
Incoming MCCB `B’
iv | Breaker control switch.
B.
(For Transformer supply)
630 amps 4 pole motorized moulded case circuit breaker with built in microprocessor based release unit for protection as per specification and with following accessories :
i. | Multifunctional meter (conzerve - EM3360 or equivalent) of accuracy class-I, with 3 nos. 630/ 5 amps 5 VA CTs to measure.
1 Set
ii. | Phase indicating light through 415/ √3 : 110V/ √3 PT, Primary/ Secondary of PT's shall be protected by 2 amps MCB’s.
1 Set
iii. | Breaker ON/ OFF/ TRIP indicating lights with control MCB’s.
1 Set
iv. | Breaker control switch.
v. | 3 nos., 315/ 5 amp CL : 1.0 CTS for APFCR.
1 Set
Bus Bars
800 amps 4 pole (35 KA) aluminium bus bars with colour coded heat shrinkable insulating sleeves.
1 Set
C. | Outgoing
i. | 200 amps 4 pole MCCB
2 Nos.
ii. | 160 amps 4 pole MCCB
3 Nos.
iii. | 100 amps 4 pole MCCB
10 Nos.
iii. | 80 amps 4 pole MCCB
2 Nos.
Spare MCCB’s for the following :
iii. | 200 amps 4 pole MCCB
3 Nos.
iv. | 160 amps 4 pole MCCB
1 No.
Capacitor Bank as per following:
Automatic and Manual mode similar or equivalent to Datar make APFC relay for 100 KVAR (2x25+1x15+2x10+3x5) of steps and suitable rating of capacitors as per specifications.
25 KVAR unit
i | 63 amps TPN MCCB
ii | 63 amps or capacitor duty 415 volts 50 HZ heavy duty contactors.
iii | "ON" / "OFF" push buttons and indicating lamps.
iv | 63 amps rating TP terminal blocks.
v | 25 KVAR mixed dielectric extra low loss type capacitor unit.
1 Set
15 KVAR unit
vi | 40 amps TPN MCCB
vii | 40 amps or capacitor duty 415 volts 50 HZ heavy duty contactors.
viii | "ON" / "OFF" push buttons and indicating lamps.
ix | 40 amps rating TP terminal blocks.
x | 15 KVAR mixed dielectric extra low loss type capacitor unit.
1 Set
10 KVAR unit
xi | 32 amps TPN MCCB
xii | 32 amps or capacitor duty 415 volts 50 HZ heavy duty contactors.
xiii | "ON" / "OFF" push buttons and indicating lamps.
xiv | 32 amps rating TP terminal blocks.
xv | 10 KVAR mixed dielectric extra low loss type capacitor unit.
5 KVAR unit
xi | 32 amps TPN MCCB
xii | 32 amps or capacitor duty 415 volts 50 HZ heavy duty contactors.
xiii | "ON" / "OFF" push buttons and indicating lamps.
xiv | 32 amps rating TP terminal blocks.
xv | 5 KVAR mixed dielectric extra low loss type capacitor unit.
1 Set
G. | Micrologic PLC:
Micrologic PLC for the load management and interlocking system. This will sense the load and accordingly send the command to AMF panel for DG ON/ OFF. The Micro PLC also taking care the interlocking system as the scheme showing on SLD.
1 Set
Note:
i. | All outgoing feeders shall have suitable range of followings (except capacitor feeders)
a. | Digital electronic ammeter with selector switch and 3 Nos. CT’s.
b. | Three phase indicating lamps through 415 V/ √3 : 110 V/ √3 PT, primary/ secondary of PT's shall be protected by 2 amps SP MCBs.
ii. | All breakers shall be electrically/ mechanically interlocked as per schematic diagram.
iii. | All MCCB’s shall be suitable for 10 KA (ICS) breaking capacity.
iv. | 415/ 110 V suitable rating control transformer shall be provided for aux. Control supply
v. | Wiring with space heater, thermostat and control MCB’s shall be provided all vertical sections of main LT panel.
vi. | All incoming feeder shall have surge protector of class - B for protections line to neutral & line to ground.
vii. | All Incoming MCCB’s feeders shall be provided with built-in microprocessor release unit with earth fault protection and time delay.
viii | All incoming as well as outgoing feeders shall have pad locking facility.
ix. | Suitable danger board shall be provided.
x. | All busbar section/ backside panels shall have pad locking facility and hinged type door.
| Main LT Panel as described above. | Set | 1
2 | ISOLATOR PANEL FOR 400kVA HT TRANSFORMER
630 amps 4 pole moulded case circuit breaker with built in microprocessor based release unit for protection as per specification and with following accessories :
i. | Phase indicating light through 415/ 110 V, PT, Primary/ Secondary of PT's shall be protected by 2 amps MCB's.
1 Set
ii. | Breaker ON/ OFF/ TRIP indicating lights with control MCB's.
1 Set
iii. | Shunt trip coil
1 Set
iv. | 3 nos. 96 x 96 mm sq. 0 - 630 A/ 5 amps CTR digital ammeter with 3 nos. 300/ 5 amps 15 VA CL : 1 CT's.
1 Set
v. | 96 x 96 mm sq. 0 - 500 Volt digital voltmeter with selector switch through above mentioned primary and secondary of PT's shall be protected by 2 amps TP MCB's.
1 Set
| Isolator Panel as described above. | Set | 1
3 | AMF CUM ISOLATOR PANEL FOR 400kVA DG SET
630 amps 4 pole moulded case circuit breaker with built in microprocessor based release unit for protection as per specification and with following accessories :
i. | Phase indicating light through 415/ 110 V, PT, Primary/ Secondary of PT's shall be protected by 2 amps MCB's.
1 Set
ii. | Breaker ON/ OFF/ TRIP indicating lights with control MCB's.
1 Set
iii. | Under voltage and Over voltage relay.
1 Set
iv. | Shunt trip coil
1 Set
v. | 3 nos. 96 x 96 mm sq. 0 - 630 A/ 5 amps CTR digital ammeter with 3 nos. 250/ 5 amps 15 VA CL : 1 CT's.
1 Set
vi. | 96 x 96 mm sq. 0 - 500 Volt digital voltmeter with selector switch through above mentioned primary and secondary of PT's shall be protected by 2 amps TP MCB's.
1 Set
vii. | Selector switch for Auto/ Manual/ Test
viii. | Selector switch for engine control OFF/ ON.
ix. | Five push buttons – start, stop, reset, test and accept.
x. | Three indicating lamps “load on set’, ‘Load on Mains’ and “ Set fail to start’.
xi. | 8 Window alarm annunicator panel with hooter, push buttons, aux. Contactors etc as required as per specification.
xii. | AMF Relay (Functions available in AMF relay shall not be provided as mentined above to avoid duplicate provision).
xiii. | Battery charger ad described in Specifications.
| Isolator Panel as described above. | Set | 1
4 | MDB - BASEMENT
Incoming:
160 amps 4 pole MCCB (isolator) with following accessories:
i. | 0-500 volts digital electronic volt meter with selector switch protected by 2 amps TP MCB's.
1 Set
ii. | 0-160 amps digital electronic ammeter with selector switch and 160/ 5 amps 10 VA, CL 1 CTs.
1 Set
iii. | Phase indicating light shall be protected by 2 amps SP MCB's.
1 Set
Bus Bars:
i. | 200 amps TPN aluminium bus bars with colour coded heat shrinkable insulated sleeve.
1 Set
Outgoing:
i. | 80 amps TPN MCCB
1 No.
ii. | 63 amps TPN MCCB
2 Nos.
iii. | 40 amps TPN MCCB
2 Nos.
iv. | 63 amps TPN MCCB (Spare)
2 Nos.
v. | 40 amps TPN MCCB (Spare)
1 No.
All MCCB's shall be of 25 KA (Ics) breaking capacity.
| MDB - B-1 described as above | Set | 1
5 | MDB - GROUND FLOOR
Incoming:
160 amps 4 pole MCCB (isolator) with following accessories:
i. | 0-500 volts digital electronic volt meter with selector switch protected by 2 amps TP MCB's.
1 Set
ii. | 0-160 amps digital electronic ammeter with selector switch and 160/ 5 amps 10 VA, CL 1 CTs.
1 Set
iii. | Phase indicating light shall be protected by 2 amps SP MCB's.
1 Set
Bus Bars:
i. | 200 amps TPN aluminium bus bars with colour coded heat shrinkable insulated sleeve.
1 Set
Outgoing:
i. | 40 amps TPN MCCB
5 Nos.
v. | 40 amps TPN MCCB (Spare)
3 Nos.
All MCCB's shall be of 25 KA (Ics) breaking capacity.
| MDB - B-1 described as above | Set | 1
6 | MDB - FIRST,SECOND FLOOR, NINTH AND TENTH
Incoming:
160 amps 4 pole MCCB (isolator) with following accessories:
i. | 0-500 volts digital electronic volt meter with selector switch protected by 2 amps TP MCB's.
1 Set
ii. | 0-160 amps digital electronic ammeter with selector switch and 160/ 5 amps 10 VA, CL 1 CTs.
1 Set
iii. | Phase indicating light shall be protected by 2 amps SP MCB's.
1 Set
Bus Bars:
i. | 200 amps TPN aluminium bus bars with colour coded heat shrinkable insulated sleeve.
1 Set
Outgoing:
i. | 80 amps TPN MCCB
1 No.
ii. | 63 amps TPN MCCB
2 Nos.
iii. | 40 amps TPN MCCB
2 Nos.
iv. | 63 amps TPN MCCB (Spare)
2 Nos.
v. | 40 amps TPN MCCB (Spare)
1 No.
All MCCB's shall be of 25 KA (Ics) breaking capacity.
| MDB -described as above | Set | 4
7 | MDB-TYPICAL FLOOR
Incoming:
100 amps 4 pole MCCB (isolator) with following accessories:
i. | 0-500 volts digital electronic volt meter with selector switch protected by 2 amps TP MCB's.
1 Set
ii. | 0-100 amps digital electronic ammeter with selector switch and 100/ 5 amps 15 VA, CL 1 CTs.
1 Set
iii. | Phase indicating light shall be protected by 2 amps SP MCB's.
1 Set
Bus Bars:
i. | 160 amps TPN aluminium bus bars with colour coded heat shrinkable insulated sleeve.
1 Set
Outgoing:
i. | 63 amps TPN MCCB
1 No.
ii. | 40 amps TPN MCCB
1 No.
iii. | 32 amps TPN MCCB
2 Nos.
iii. | 32 amps DP MCB
11 Nos.
iv. | 100 amps TPN MCCB (Spare)
1 Nos.
v. | 32 amps DP MCB (Spare)
3 Nos.
All MCCB's/ MCB's shall be of 25 KA (Ics) breaking capacity.
| MDB-TYPICAL FLOOR described as above | Set | 6
8 | FINAL DISTRIBUTION BOARDS:
Supply, installation, testing and commissioning of the following FDB's fabricated out of 1.6 mm thick CRCA sheet steel, double door construction, powder coated with approved shade and partitions to segregate phases. Approved lockable covers with padlocking arrangement for each phase, recessed in wall or surface mounted final distribution boards of the following description:
OPTIONAL -Class - C (For SPN final distribution boards) (lines to Neutral) (Neutral to earth) suitable for 1 Phase as per specification and Class - C (For TPN final distribution boards) (lines to Neutral) (Neutral to earth) suitable for 3 Phase as per specification
8.1 | Type A
| 10 way VTPN DB, 10 Nos. 10/ 16/ 20 amps SP MCB’s per phase with 3 Nos. 63 amps DP RCCB’s of 30 mA leakage current and 1 no. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | Nos. | 2
8.2 | Type B
| 10 way TPN DB, 10 Nos. 10/ 16/ 20 amps SP MCB’s per phase with 3 Nos. 63 amps DP RCCB’s of 30 mA leakage current and 1 no. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | Nos. | 2
8.3 | Type C
| 10 way TPN DB, 8 Nos. 10/ 16/ 20 amps SP MCB’s per phase with 3 Nos. 63 amps DP RCCB’s of 30 mA leakage current and 1 no. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | Nos. | 4
8.4 | Type D
| 6 way TPN DB, 6 Nos. 10/ 16/ 20 amps SP MCB’s per phase with 3 Nos. 40 amps DP RCCB’s of 30 mA leakage current and 1 no. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | Nos. | 6
8.5 | Type E
| 6 way SPN DB, 6 Nos. 6/10 amps SP MCB’s with 1 no. 20 amps DP RCCB of 30 mA leakage current and 1 no. 20 amps DP MCB as incomer. Indication light with MCB shall be provided. | Nos. | 2
8.6 | Type F
| 8 way SPN DB, 8 Nos. 10/20 amps SP MCB and 32 amps DP RCCB’s of 30 mA leakage current and 1 No. 32 amps DP MCB isolator as incomer including cu.bus bars. | Nos. | 75
8.7 | Type-L (for external lighting with IP-55/ corridor lighting with IP-52)
Incomer : 1no. 63A 4P MCB isolator with 100A 4P insulated copper busbars.
| Out going : 2 sets each having 6 way TPN DB 6 Nos. 10 amps SP MCB per phase as outgoing with 3 nos. 40 amps DP RCCB of 30 mA leakage current plus 1 No. 40 amps TP Contactor controlled through 0-24 hour timer and 1 No. 40 amps 4 pole isolator as incomer. | Sets | 2
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
D | EARTHING INSTALLATION (FOR POWER DISTRIBUTION SYSTEMS, UPS SYSTEM, DG SETS & LOW VOLTAGE SYSTEM
1 | Supply and fixing of following bare copper/ wires including all necessary fixing accessories and effecting connections as per specifications.
1.1 | 25 x 6 mm thick copper tape. | RM | R.O.
1.2 | 25 x 3 mm thick copper tape. | RM | 650
1.3 | 8 SWG Copper wire | RM | 450
2 | Supply and fixing of following bare GI strip including all necessary fixing accessories and effecting connections as per specifications.
2.1 | 50 x 6 mm thick GI tape. | RM | 150
2.2 | 25 x 3 mm thick GI tape. | RM | 450
3 | Providing and laying of 600 x 600 x 3.15 mm thick tined copper plate electrode, with 2 Nos 50 x 6 mm copper strips from earth plate electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 x 500 mm with concrete base CI heavy duty/ chequered plate manhole cover with frame painted with bitumastic paint and packing with mixture of charcoal and common salt around plate electrode including digging of pit upto permanent moisture level and as per soil condition but not less than 3 meters and back filling as required. | Nos. | 18
4 | Supply and laying of following 1100 volts grade PVC insulated sheathed copper conductor unarmoured cable including copper thimbles, fixing hardware as required.
4.1 | Single core 35 sq.mm Green colour cable | RM | 50
4.2 | Single core16 sq.mm Green colour cable | RM | 50
4.3 | Single core 6 sq.mm Green colour cable | RM | R/O
5 | Supply and laying of GI pipe under road/ paved area crossing etc. including excavation back filling ramming and making good.
5.1 | 50 mm dia pipe. | RM | 25
5.2 | 100 mm dia pipe. | RM | 100
5.3 | 150 mm dia pipe. | RM | R/O
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
E | LIGHTNING PROTECTION SYSTEM
1 | Supply and fixing of following Erico/ LPI or equivalent make enhanced air terminals as per specifications.
1.1 | ESE terminal 1 stainless steel for hostile environment application suitable for coverage of 79M radius (Protection level - 1) as per specification. | No. | 1
1.2 | Insulated 2 M FRP Mast black. | No. | 1
1.3 | Inline coupling as per specification. | No. | 1
1.4 | Mast, AL, 2 M mast base, welded together. | No. | 1
1.5 | Guykit with W.R. grips. | No. | 1
2 | Supply and fixing of following down conductor with fixing accessories:
2.1 | 70 mm bare flexible copper conductor. | RM | 90
2.2 | Upper termination kit. | No. | 1
2.3 | Lower termination kit. | No. | 1
2.4 | Supply of conductive saddles. | Nos. | 30
2.5 | Fixing for conductive saddles. | Nos. | 30
2.6 | Satinless steel cable ties. | No. | 2
3 | Supply and installation of following earthing compounds, tapes, rods & clamp as per specification.
3.1 | Earth Gel 10 Kg Kit. | No. | 2
3.2 | Copper earth tape of 25 x 3 mm | RM | 10
3.3 | Earth rod clamp. | No. | 2
3.4 | Copper bonded ground rod 10ftx5/8 inch dia model. | No. | 2
3.5 | Supply and laying of medium class GI pipe under road/ paved area crossing etc. including excavation back filling ramming and making good (depth of excavation shall be minimum 750 mm).
a. | 75 mm dia pipe | RM | 30
3.6 | Providing and fixing of lightning event counter (without battery) as per specification. | No. | 3
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
F | SUPPLY AND INSTALLATION OF LIGHTING FIXTURE
Supply, Installation, testing and Commissioning of the following lighting fixtures with all fixing accessories etc. as required.
1 | Recessed downlight LED (Light Emitting Diode) of 10 W, 230V, direct light emission, housing with ceiling trim, in die-cast aluminium, white, satin diffuser, passive cooling, electronic control gear with Protection class I, IP20 / IP44. | Nos. | 900
2 | Recessed downlight LED (Light Emitting Diode) of 18 W, 230V, direct light emission, housing with ceiling trim, in die-cast aluminium, white, satin diffuser, passivecooling, electronic control gear,Protection class I, IP20 / IP44. | Nos. | 20
3 | Supply, fixing, testing and commissioning of Recess mounted 38 W (600 x 600 mm) LED luminaries with complete PMMA difuser in metallic frame, held securely to the main body, epoxy, white powder coated CRCA sheet steel housing, pre wired with vacuum presser impregnated copper ballast. RATED LIFE SHOULD BE MORE THAN 50000 BURNING HOURS (WITH REPLACEMENT GUARANTEE OF THE SUPPLIER) | Nos. | 110
4 | Bulk head lighting fixtures equivalent to Philips Cat. No. NXC-101 with 11 watt CFL lamps and accessories as required. | Nos. | 20
5 | Lighting technologies LED Wand 18W 4000K 4ft linear slim LED batten fixture with cascading option for wall mounting arrangement. Made of extruded aluminium housing, uniform brightness with Injection molded PC diffuser, Synergistic coupling of silicon potted drivers and Aluminum die cast housing powder coated through nano technology delivers system durability to support LED life of 50,000 hrs as per L70 std. Highest Sytem efficacy of 100Lm/W. with all necessary accessories for mounting. | Nos. | 60
6 | Lighting technologies LED Wand 28W 4000K 4ft linear slim LED batten fixture with cascading option for wall mounting arrangement. Made of extruded aluminium housing, uniform brightness with Injection molded PC diffuser, Synergistic coupling of silicon potted drivers and Aluminum die cast housing powder coated through nano technology delivers system durability to support LED life of 50,000 hrs as per L70 std. Highest Sytem efficacy of 100Lm/W. with all necessary accessories for mounting. | Nos. | 100
7 | Industrial lighting fixture as Philips Cat No. TKC203/236 EBT or equivalent complete with 2x36 watt fluorescent lamp and accessories as required. | Nos. | 20
8 | Flood lighting fixture as Philips Cat No. QVF135/MHNTD70W or equivalent complete with 1x70 watt lamp and accessories as required. | Nos. | 10
9 | Self contained single sided exit sign for wall/ ceiling/ pendant cantilever mounting with 9 W CFL tube for non maintained battery backup emergency lighting for 3 hours duration Thorn EXB3, Prolite make or equivalent. | Nos. | 12
10 | Self contained double sided exit single for wall/ ceiling/ pendant cantilever mounting with 9 watt CFL tube, non maintained battery backup 3 hours duration Thorn EXB3, Prolite make or equivalent. | Nos. | 30
11 | Self contained emergency light for wall/ ceiling/ pendant cantilever mounting with 9 watt CFL tube, non maintained battery backup 3 hours duration | Nos. | 20
Note: | All Fluorescent lighting fixtures compact flourescent lighting fixtures shall be provided with electronic ballast and TLD/ T5/ CFL lamp as per specifications.
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
G | HV INSTALLATION
I | SUPPLY AND INSTALLATION OF SUB-STATION EQUIPMENT
1 | 11 KV SWITCHGEAR
a | 11 KV VCB
Supply, installation, testing and commissioing of 11 KV, Breaker Vacuum Circuit Breaker Panel Board comprising of 1 No. incoming & 1 No. outgoing breakers. Each incoming, outgoing breaker panel shall be totally enclosed, 2 mm thick CRCA sheet steel, floor mounting, free standby, dust and vermin proof indoor type complete as per specification and as described.
Incoming Panel:
i. | 1 no. 630 amps, 11 KV vacuum circuit breaker with breaking capacity of 350 MVA, motorised spring charged and manual closing mechanism rated at 230 volt single phase AC supply while closing and tripping coil shall operate in 24 volts DC supply.
ii. | 3 nos. double core current transformer 150/ 5 amps epoxy cast resin insulated class of insulation E.
Core 1-15VA burden class 1.0 for metering.
Core 2-15VA burden class 5P10 for protection
iii. | 3 nos. line PT 11 KV/ √3, 110V/ √3, 100VA class 1.0 epoxy cast resin type.
iv. | IDMT relay with 3 O/C and 1 E/F element.
v. | 1 no. digital voltmeter (0-12 KV) with selector switch (96mm x 96mm).
vi. | 1 no. digital ammeter (0-150 Amp) with selector switch (96mm x 96mm).
vii. | 1 no. digital power factor meter.
viii. | 1 no. electronic digital type energy analyzer having 30 days memory and parameters of KW, KWH, KVAH, KVARH power factor, frequency etc.
ix. | 1 no. breaker control switch
x. | 1 set of following indicating lamps
- | Red, Yellow and Blue for phase indication
- | Amber for trip indication
- | Red `ON’ Green `OFF’
- | Spring charge indication
- | Auto trip indication
xi. | 1 no. hooter
xii. | 1 set of fuses, ferrules, wiring etc. as required.
xiii. | Suitable arrangement for termination of 3 core 240 sqmm 11KV XLPE cable
| 11KV breaker panel, described as above | Set | 1
2 | Supply, installation, testing and commissioning of 400 KVA capacity 11/0.433 KV, 3 phase, 50 Hz copper wound, step down oil type transformer with OLTC, with RTCC Panel,vector group Dyn-11 having cable end box suitable for 3 core 240 Sqmm XLPE al. conductor 11 KV on Hi side and provision for terminating bus duct/ cables LT side with all fitting and accessories, WTI alarm and trip wiring complete with limit switches for enclosure door with wiring for interlocking with the HT breakers as per specifications. | Nos. | 1
3 | Supply, installation, testing and commissioning of 200 AH capacity 24 volts DC hermetically sealed maintenance free lead acid batteries duly charged. | Set | 1
4 | Supply, installation, testing and commissioning of battery charger unit with provisions of Boost Charing, and Float charging. Suitable for 240 V single phase + 10% AC, 50 Hz power supply as per specifications. | Set | 1
5 | Supply and fixing in position the approved “Shock Treatment Charts” written in English and Local Language. These charts shall be framed in teak wood frame and covered with glass. | Nos. | 1
6 | Supply and fixing in position the fire extinguishers carbon-di-oxide type 2.5 Kgs capacity. | Nos. | 1
7 | Supply and fixing in position the best quality Danger Boards of approved shape and size as specified by Local Electricity Authorities written in English & Local Languages. | Nos. | 1
8 | Supply and fixing in position 1000 mm wide rubber matting of 11 KV grade as per electricity rules. | RM | 10
9 | Supply and fixing of fire buckets 5 nos. in each set duly filled with fine sand and fixed on an angle iron frame as per requirement of local authorities. Fire buckets shall be painted red from outside and white from inside with additional handle at the bottom. | Sets | 1
10 | Supply and fixing in position the approved single line diagram framed in 1000 x 800 mm size glass frame in the sub station. | Nos. | 2
11 | Supply of first aid box of approved make as per specification. | Nos. | 2
12 | Supply of tool kit with 1 pair 11 KV rubber hand gloves of approved make. | Nos. | 2
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
II | HT CABLES & LT CONTROL CABLES
1 | Supplying and laying following size 11 KV grade XLPE aluminium conductor armoured cables laid over MS supports in existing trenches.
1.1 | 3C x 240 sq.mm 11 KV, XLPE cable (between metering panel room to HT panel and HT panel to transformers). | RM | 100
2 | Supplying and making cable end terminations for the following size of 11 KV grade, XLPE aluminium conductor armoured cable including termination kit complete heat shrinkable sleeve etc.
2.1 | 3C x 240 sq.mm 11 KV XLPE cable (indoor) | Nos. | 4
3 | Supplying, laying GI sleeves of following sizes:
3.1 | 150 mm dia | RM | R/O
3.2 | 200 mm dia | RM | 45
4 | Supplying and laying of following 1100 volts grade PVC insulated sheathed copper conductor armoured control cables in existing trenches cables trays, clamped on wall with suitable saddles, fixing bolts, including testing and commissioning.
4.1 | 4 Core 2.5 sq mm PVC insulated copper conductor armoured control cables. | RM | 100
5 | Cable end termination of the following PVC insulated sheathed aluminium conductor armoured cables of 1100 volt grade including supplying and fixing of crimping lugs. Double compression glands with earthing provision and cable sockets.
5.1 | 4 Core 2.5 sq.mm Control cable | Nos. | 4
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
III- | HV - EARTHING FOR SUBSTATION
1 | Supplying and fixing of following bare copper tapes including all necessary fixing accessories and effecting connections.
1.1 | 50 mm x 6 mm thick copper tape. | RM | 150
1.2 | 25 mm x 6 mm thick copper tape. | RM | R/O
2 | Supplying and fixing of following insulated copper tapes including all necessary fixing accessories and effecting connections.
2.1 | 50 mm x 6 mm thick copper tape. | RM | 35
3 | Providing and installation of earthing stations at locations as called for including providing and laying 600 x 600 x 3.15 mm thick tinned copper electrode with 2 Nos 50 x 6 mm thick copper strip, from earth electrode to inspection chamber, 50 mm dia medium class GI pipe CI/ chequered plate funnel with 20 gauge GI wire mesh, masonry chamber 1000 x 500 mm with concrete base, CI chequered plate manhole cover with frame and bitumastic paint and packing of mixture of charcoal and common salt around plate electrode complete with digging of pit upto permanent misture level but not less than 3 metres and back filling as required. | Nos. | 8
4 | Maintenance free earthing electrode/ Chemical earthing
| Providing and laying of 14.35 mm dia and 3 meter length copper bonded earth rod in 150 mm dia. in an augured hole in ground, surrounded by ground enhancement material as per specification. Inspection chamber shall be of 400 x 500 mm with concrete base CI manhole cover with frame painted with bitumastic paint. 2 Nos. of 50 x 6 mm cross section & 300 mm long copper strip to be clamped with copper claded rod electrode have sufficient nos (But not less than 4 Nos.) of 10 mm dia. GI nuts & bolts for connection to the equipment/ interconnection to the other pits to form equi-potential bonding. The pH value of ground enhance material shall be 6.9 to 7.2 of 1000gm/ lit @ 20 deg.c. The minimum 30 Kg of ground enhancement material shall provided for each electrode. | Nos. | 4
5 | Supply and laying medium class GI pipe under road/ paved areas/ wall crossing etc. including earth excavations refilling, ramming and making good as approved.
5.1 | 150 mm dia GI pipe | RM | 10
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
H | CONDUITING AND CABLING FOR TELEPHONE SYSTEM
1 | Supply, installation, testing and commisioning of the following incoming telephone cables.
1.1 | 100 pair 0.61 mm dia tinned copper armoured cable | RM | 120
2 | Supply, installation, testing and commissioning of Category 5 Riser cable consisting of multiple core or solid copper conductors of 24 AWG size insulated with expanded polyethylene covered by a PVC skin and inner shielding for grounding. The core shall be covered by a layer of plastic tape and overlaid with a corrugated PVC plastic. The cable shall be as per the specifications laid down in the tender.
2.1 | 25 pair riser cable | RM | 450
3 | Supply, installation, testing and commissioning of 24 AWG hook-up wire of solid annealed copper conductors individually insulated with PVC sheathe. The electrical DC resistance shall be 52 ohm per 100 feet with mutual capacitance not exceeding 0.015 per 1000 feet. One pair hook up wire shall be tied in such a way that with repeated use, twists should not start unwinding.
3.1 | 1 pair hook up wire | RM | 50
3.2 | 4 pair hook up wire | RM | 50
4 | Supply, installation, testing and commissioning of 4 pair Category 6 UTP cable consisting of 23 AWG solid copper conductors and as per the specification. The cable should have flexible jacket and ripcord for easy stripability. | RM | 2500
5 | Supply, installation, testing and commissioning of Category 6 IDC patch panle prepackaged with wiring block with legs, insert labels, label holders, jumper troughs, metal back panel duct assembly, screws washers and an instruction sheet for termination of incoming pairs. Rate shall include suitable size of lockable 1.6mm thick CRCA sheet steel enclosure duly powder coated.
5.1 | 100 pair wiring block | Nos. | 2
6 | Supply and installation, testing and commissioning following size KRONE make telephone tag block in lockable 16 gauge sheet steel enclosure complete as required.
6.1 | 10 pair Krone type tag block | Nos. | R/O
6.2 | 20 pair Krone type tag block | Nos. | R/O
7 | Supply and installation of flush mounted Category 6 T 568 A or B outlet. The plastic shall be high impact, flame-retardant UL rated thermoplastic. Dust cover/ Blank shall be provided to protect unused face plate openings. Termination cap and plastic cover shall be provided to protect jack wiring.
7.1 | Single outlet face plate with RJ-11 jack | Nos. | 210
7.2 | Double outlet face plate with RJ-11 jack | Nos. | 10
8 | Providing and laying the following HDPE pipe of 6 Kg/ Cm2 working pressure laid in ground including cost of digging, 150 mm sand all around the pipe, brick protection and back filling including all accessories i.e. bends, reducers, flanges of approved make and design complete as required.
8.1 | 75 mm OD with 2.3 mm wall thickness | RM | R/O
8.2 | 100 mm OD with 2.9 mm wall thickness | RM | 100
9 | Supply, installation, testing and commisioning of the following telephone cables.
9.1 | 50 pair 0.61 mm dia tinned copper armoured cable | RM | R/O
9.2 | 100 pair 0.61 mm dia tinned copper armoured cable | RM | R/O
10 | Providing and fixing in position the following 16 gauge MS conduits concealed or exposed as called for including all acessories i.e. bends, junction boxes, outlet boxes with cover plates of approved make and design.
10.1 | 20 mm dia conduit | RM | R/O
10.2 | 25 mm dia conduit | RM | 3000
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
I | CONDUITING AND CABLING FOR DATA SYSTEM
1 | Supply and installation of following 19 inch rack for ethernet switches with A.C. distribution box, wire manager, fan tray, lockable front tinted glass door and two pair angle to support the switch installed in the rack.
1.1 | 18 U Rack | Nos. | 1
2 | Supply, installation, testing and commissioning of 24 port Ethernet switch as per specification. | Nos. | R/O
3 | Supply, installation, testing and commissioning of following Category 6, IDC patch panel prepackaged with wiring block with legs with legs insert labels, label holders, jumper troughs, metal back panel, duct assembly, screws, washers and an instruction sheet for termination of incoming pairs.
3.2 | 24 port jack panel | Nos. | 5
4 | Supply and installatlion of wire manager suitable for mounted on 19 inch rack. | Nos. | 2
5 | Supply, installation, testing and commissioning of 4 pair Category 6A LAN cable consisting of 24 AWG solid copper conductors and as per the specification. The cable shall have flexible jacket and ripcord for easy Stripability. | RM | 4500
6 | Supply and fixing of 16 guage MS conduits in following sizes including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab cutting chasis and making good or surface mounted including all fixing hardware.
6.1 | 20 mm dia | RM | R/O
6.2 | 25 mm dia | RM | 2400
6.3 | 32 mm dia | RM | R/O
7 | Supply of following type tools :
7.1 | 5 pair tools set | Set | 2
7.2 | Single pair tools set | Set | R/O
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
J | BILL OF QUANTITIES FOR DIGITAL MATV SYSTEM
1 | Supply , installation, testing & commissioning of Digital SMATV Headend/Multiplexer/ SMPS/ Chasis-Rack/Vent Fan (64 AV & 16-Transponders for FTA Channels) | Lot | 1
2 | Supply of the following Items as required to complete the installation in all respect as per specification.
2.1 | Digital Satellite Receivers for FTA channels | Nos. | 1
2.2 | 12' dia C Band high gain Satellite Dish Antennae | Nos. | 1
2.3 | Digital LNBC with extended C band | Nos. | 3
2.4 | Dual Feed Horn for LNBC | Nos. | 1
2.5 | Microwave Amplifier 950 - 2150 MHZ | Nos. | 1
2.6 | Microwave Power Divider for 2 way/4 way/6 way | Nos. | 1
2.7 | 120 CM Ku band dish antenna | Nos. | 1
2.8 | Ku band quattro LNB & accessories | Nos. | 1
3 | For Control Room
3.1 | Equipment Rack for Decoders/DSR with power points/ventilation fans/wheel-lock | No. | 1
3.2 | PVC Channel Cable management/tagging-etc. of | Lot | 1
Schneider/MK or equivalent.
4 | Distribution
4.1 | RG-11 Co-Axial Cable | RM | 550
4.2 | RG-6 Co-Axial Cable | RM | 1250
4.3 | Die-cast Aluminium Bi-directional Splitters 2 way (S2) | Nos. | 10
4.4 | Die-cast Aluminium Bi-directional Splitters 4 way (S4) | Nos. | 2
4.5 | Die-cast Aluminium Bi-directional Tap off 2 way (T2) | Nos. | RO
4.6 | Die-cast Aluminium Bi-directional Tap off 4 way (T4) | Nos. | 20
4.7 | F5 Type Connectors for RG-6 Cable | Nos. | 100
4.8 | F7 Type Connectors for RG-11 Cable | Nos. | 46
4.9 | Cable Jointers - F-type for RG-6 or RG-11 Cable | Nos. | 20
4.1 | 75 Ohms End Terminators | Nos. | 20
4.11 | RF Leads from TV to wall outlets | Nos. | 80
4.12 | 19" LCD TV as Monitor | Nos. | 1
4.13 | RF Combiner/Multiplexer/Filter | Nos. | 1
4.14 | RF Amplifier Broadband(47-860MHZ) | Nos. | 2
4.15 | 24 port switches with compression connectors with complete accessories | Lot | 1
5 | Supply and fixing following signals outlets with grid plate in 2 MM thick GI box complete (Cover plate shall match the colour, size and make of wiring accessories to be used in the project)
5.1 | TV Signal Outlet | Nos. | 360
6 | Supply and fixing of 25mm dia. 2mm thick embeded heavy duty FRLS PVC conduits of following sizes including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab, cutting chasis and making good including all fixing hardware.
6.1 | 20 mm dia 2mm thick PVC | RM | RO
6.2 | 25 mm dia 2mm thick PVC | RM | 3500
6.3 | 32 mm dia 2mm thick PVC | RM | 1000
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
K | UPS SYSTEM
Supply, testing & commissioning of the following rating of UPS as per specifications & complete in all respects.
1 | 1 x 30 KVA (three phase input & three phase output) UPS system configuration with isolation transformer & static by pass facility with 20 minutes battery back up for lighting load application. | No | 1 |  |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
L | SUPPLY AND INSTALLATION OF DG SET WITH ACCESSORIES
1 | Supply, installation, testing & commissioning of 400 KVA continuous rating (Prime Rating) diesel generating set in acoustic enclosure radiator cooled alongwith day oil fuel tank with fuel piping to end from DG set including vibration mounts, base frame, hardware Batteries, Engine control panel with accessories first fill of lube oil residential silencer, flexible connection bellow/ expansion joints etc. complete and with all associated equipment/ work as per specifications. | Set | 1
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
M | SUPPLY AND INSTALLATION OF LIGHTING CONTROL EQUIPMENT
Supplying, installation, testing and commissioning of following lighting control equipment and accessories complete as per specification.
1 | PIR Digital - Slimline flush Sensor with a range of 6 meter dia. | Nos. | 20
| TOTAL CARRIED TO SUMMARY |  |  |  |  | 0
| TOTAL FOR ELCTRICAL AND ALLIED WORKS |  |  |  |  | 0
SANITARY AND PLUMBING WORKS
A. | SANITARY FIXTURES & FITTINGS:
Note:
i. | Detail of Sanitary fixture are for the information of the Contractor, however model / makes of all sanitary fixture shall be selected by Architect / Interior designer / client and the same shall be binding for execution.
ii. | No additional Cost, all Providing and Fixing cost shall be paid for change in type of sanitary fixture or fitting.
iii. | Provision of extension piece for final connection of CP fitting shall be supplied and installed by the contractor accordingly (as required)
1 | Providing and Fixing, testing and commissioning of white vitreous China wall mounting type European water closet including providing & Providing and Fixing C.P. bolts, nuts, Cast Iron chair (painted with two coats of enamel paint over a coat of primer) or other hanging arrangements, bakelite / poly propylene seat & cover with C.P. hinges & rubber buffers, C.P. brass screw, washer with all accessories. Including cutting & making good the walls, floors, slab wherever required. | Nos. | 85
2 | Providing and Fixing, testing & commissioning of concealed type cistern with dual flush (3/5 ltr.) facility comprising of actuator button facia assembly including brass / SS screws and washer complete, providing protection cover over cistern, cutting and making good the walls wherever required. | Nos. | 85 |  |  | 0
3 | Providing and Fixing, testing & commissioning of ABS Rinsing spray with regulator of approved quality with plastic flexible pipe 1.5 m long, wall hook complete as required. | Nos. | 85
4 | Providing and Fixing first quality white vitreous china oval / round / square wash basin (size as per architectural drawing) for under counter mounting, specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including filling gap between counter and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. | Nos. | 80
5 | Providing and Fixing first quality white vitreous china wall mounting wash basin (size as per architectural drawing) including providing & Providing and Fixingspecially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. | Nos. | 4
6 | Providing C.P. brass single lever basin mixer with / without pop up waste system complete. | Nos. | 80
7 | Providing and Fixing, testing & commissioning of C.P. brass eurometic self closing pillar tap. | Nos. | 10
8 | Providing and Fixing, testing and commissioning of bathing facucets including necessary wall chases and making good.
8.1 | Providing and fixing of Concealed bath shower divertor, faucet, 115 mm long bend pipe, overhead shower and wall flanges complete (As Per Green Building,Shower <1.2 GPM). | Nos. | 84
8.2 | Providing andfixing of Concealed thermostatic mixer with valves & divertor for overhead shower & hand shower (As Per Green Building,Shower <1.2 GPM). | Nos. | 84
8.3 | Providing and fixing of Single lever wall divertor assembly with non-return valves (As Per Green Building,Shower <1.2 GPM) | Nos. | 84
8.4 | Providing and fixing of Concealed stop valves with wall flanges | Nos. | 84
8.5 | Providing and fixing of Bath Tub Spout / Spout | Nos. | 84
8.6 | Providing and fixing of Overhead shower with short / long arm and wall flange | Nos. | 84
8.7 | Providing and fixing of Overhead drencher shower, ceiling mounted | Nos. | 84
9 | Providing and fixing of SS 304 SS shower channel with grating (polished surface), socket type outlet (50 mm dia), slope towards socket, effective tray depth 20 mm, width 70 mm with following length.
9.1 | 900 mm dia (Approximate) | Nos. | 84
10 | Providing and Fixing, testing and commissioning of white viterous china large flat back / half stall urinal including providing & Providing and Fixing CI / MS bracket (duly painted with 2 coats of paints over a coat of primer), including CP brass waste with dome type grating, CP cast brass bottle trap with extension piece, wall flanges complete with all accessories. | Nos. | 10
11 | Providing and Fixing, testing and commissioning of white vitreous china large urinal partition including providing & Providing and Fixingconcealed CI bracket, cutting and making good. | Nos. | 6
12 | Providing and Fixing of battery operated automatic urinal flushing systems for urinal flushing complete as mentioned above. | Nos. | 10
13 | Providing and Fixing, testing and commissioning of sink including providing & Providing and FixingC.I./M.S. Brackets (duly painted with 2 coats of paint over a coat of primer) C.P. cast brass bottle trap with extension piece, rubber adaptor, wall flange, union, C.P. brass chainrubber plug & making good.
13.1 | Stainless Steel sink w/o drain board | Nos. | 4
13.2 | Stainless steel sink with drain board. | Nos. | 2
14 | Providing and Fixing, testing and commissioning of C.P. brass wall / counter mounted sink mixer with C.P. wall flange, overhead swinging spout complete as required and making good (As Per Green Building, <1.8 GPM ). | Nos. | 2
15 | Providing and Fixing of white viterous china Janitor sink of size 470 x 370 x 180mm deep including providing & Providing and FixingCI/MS brackets (duly painted with 2 coats of paint over a coat of primer) C.P. cast brass bottle trap with extension piece, rubber adopter, wall flange, union, C.P. brass chain rubber plug complete as required. | Nos. | 4
16 | Providing and Fixing solid state, no touch operating, fully hygienic hand drier of approved shade with double blower, continous repeat usage,time delay, summer & winter control 'including providing necessary brackets, cable from drier to Plug, Plug to key and lock etc. complete as required. | Nos. | 6
17 | Providing and Fixing beveled edge mirror of superior quality glass 5.5 mm thick (of approved make) with 3mm thick wooden ply of required sizes. Including wooden beeding around the mirror, wooden clets, C.P brass screws and washer etc. Complete as required as per architect requirement. | Nos. | 86
18 | Providing and Fixing S.S. shower curtain rail with CP brass / SS wall brackets C.P brass screw complete as required.
18.1 | Size 1800 mm x 25 mm dia | Nos. | 86
19 | Providing and Fixing Recessed type S.S. toilet paper holder with PVC rawl plug & C.P. brass screw complete as required. | Nos. | 86
20 | Providing and Fixing recessed type S.S. soap dish with grab bar with PVC rawl plug & C.P. brass screw complete as required. | Nos. | 86
21 | Providing and Fixing push type liquid soap dispenser with PVC rawl plug & C.P. brass screw complete as required. | Nos. | 86
22 | Providing and Fixing C.P brass Bottle opener. | Nos. | 86
23 | Providing and Fixing C.P. brass twin coat hook with PVC rawl plug & C.P. brass screw complete as required. | Nos. | 86
24 | Providing and Fixing C.P brass deodourizer. | Nos. | 86
25 | Providing and Fixing deodoriser system with turbo fan, battery & cartridge including wall mounting arrangement complete as required. | Nos. | 10
26 | Providing and Fixing, testing and commissioning of 15 mm dia C.P. brass 2 way bib cock with C.P. wall flange of approved quality and making good (As Per Green Building, Hand Wash <1.2 GPM ). | Nos. | 50
27 | Providing and Fixing, testing and commissioning of C.P. brass angle valve with C.P. wall flange, Nut and Washer etc. complete as required. | Nos. | 400
28 | Providing and Fixing, testing and commissioning of C.P Copper connection 375 mm long including nuts and washers and making connection to fixtures and fittings complete as required. | Nos. | 180
29 | Providing and Fixing adjustable type wash basin for handicap toilet complete with brackets, tracks, waste pipes and other accessories complete as required. | Nos. | 4
30 | Providing and Fixing 2 Nos. support arms and backrest to mounted on the track (vertically and laterally) for handicap toilet complete as required. | Nos. | 4
31 | Providing and Fixing raised toilet seat with cover for handicap toilet | Nos. | 2
32 | Providing and Fixing 35 mm dia powder coated steel grab bar. | Nos. | 2
33 | Providing and fixing of steel enamel bath tub including waste overflow set, chain plug, cast brass P/S trap with overflow arrangement, legs complete as required.
33.1 | Apron type bath tub | No. | 66
33.2 | Free standing bath tub | No. | RO
34 | Providing and fixing of sensor based automatic battery operated hot & cold water tap with solenoid valve at inlet, Doppler based sensor, control box complete with all flexible pipes & accessories. | Nos. | 10
| Total Carried to Summary |  |  |  |  | 0
B | COLD WATER SUPPLY : (INTERNAL / EXTERNAL)
1 | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 40 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.
Cost shall be inclusive of (a)Making maximum of 7.5 x 7.5 cm chase in wall and floors for the pipe, making good the same by using 1:2 cement mortar over the wire mesh and providing protection to embedded pipes and fittings (in wall chase) by wrapping two layers of 400 micron polythene sheet including proper overlaps on joints complete as required or (b) Fixing/supporting the pipes (& fittings) at wall/ceiling level supported by galvanized clamps, fastener, hangers etc, as per specification. Exposed pipes to be painted of legends with direction arrow. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Manager's / Consultant requirement.
1.1 | 1/2" dia (15 mm) | RM | 350
1.2 | 3/4" dia (20 mm) | RM | 100
1.3 | 1" dia (25 mm) | RM | 150
1.4 | 1.1/4" dia (32 mm) | RM | 50
1.5 | 1.1/2: dia (40 mm) | RM | 100
1.6 | 2" dia (50 mm) | RM | 150
1.7 | 2.1/2" dia (65 mm) | RM | 60
1.8 | 3" dia (80 mm) | RM | 80
1.9 | 4" dia (100 mm) | RM | 150
1.1 | 6" dia (150 mm) | RM | QR
2 | Providing & fixing male/ female screwed end full way lever operated forged brass ball valve of brass body with forged brass hard chromeplated ball & teflon seat tested to a pressure 30 Kg / sqcm with (threaded joints) complete as required.
2.1 | 15 mm dia | Nos. | 25
2.2 | 20 mm dia | Nos. | 10
2.3 | 25 mm dia | Nos. | 60
2.4 | 32 mm dia | Nos. | 10
2.5 | 40 mm dia | Nos. | 18
2.6 | 50 mm dia | Nos. | 10
3 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories tested to a pressure not less than 15 Kg./sqcm including rubber gaskets, flanges, nuts, bolts & washers complete as required.
3.1 | 50 mm dia | No. | 2
3.2 | 65 mm dia | No. | 8
3.3 | 80 mm dia | No. | 8
3.4 | 100 mm dia | No. | 4
3.5 | 150 mm dia | No. | QR
4 | Providing, fixing , testing and commissioning water meter with direct reading dial in KL with all necessary fitting such as threaded pieces, unions pressure gauge, isolation cock, flanges piece for future removal, flanges / unions complete with all necessary testing charges and obtaining test certificates from municipal authorities, on following size pipe lines (1 no. strainer shall be provided at inlet & outlet and cost shall be inclusive for the same).
4.1 | 25 mm dia (Gun metal) | No. | QR
4.2 | 32 mm dia (Gun metal) | No. | 1
4.3 | 50 mm dia (CI) | No. | QR
4.4 | 65 mm dia (CI) | No. | QR
4.5 | 80 mm dia (CI) | Nos. | 2
5 | Making water supply connection to kitchen / laundry equipment, appliances, coolers etc. including necessary fittings, (pipes and valves to be paid separately).
5.1 | 15 mm to 25 mm dia | Nos. | 20
5.2 | 32 mm to 50 mm dia | Nos. | 10
6 | Providing and fixing stainless steel hose connection with flange / union connection. | Nos. | 20
7 | Providing & fixing Auto Air vent for cold water supply risers, suitable for pressure not less than 15 Kg/Sq.cm.
7.1 | 15 mm dia | Nos. | 11
7.2 | 20 mm dia | Nos. | 2
8 | Providing and fixing 600 mm dia ductile iron (heavy duty) water tank circular cover with frame (as per EN-124) with lockable arrangement complete in all regards (Total WT of cover and frame tobe not less than 85 kg). | Nos. | 10
9 | Providing and Constructing brick masonary chamber (for housing valves, Meters etc.) of brick work with bricks of class 75 with cement mortar 1:5 (1 cement:5 fine sand) plastering internal face & (with a floating coat of neat cement) cement mortar 1:3 (1 cement: 3 fine sand and rough plaster on outer face. R.C.C top slab with medium duty D.I. manhole cover and frame of 600 mm dia (weight : 60 KG). Including excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material complete as required. (All sizes are clear internal sizes).
9.1 | Size 1000 x 800 x 1200 mm deep | No. | 10
| Total Carried to Summary |  |  |  |  | 0
C | HOT WATER SUPPLY:
1 | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 40 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.
Cost shall be inclusive of (a)Making maximum of 7.5 x 7.5 cm chase in wall and floors for the pipe, making good the same by using 1:2 cement mortar over the wire mesh and providing protection to embedded pipes and fittings (in wall chase) by wrapping two layers of 400 micron polythene sheet including proper overlaps on joints complete as required or (b) Fixing/supporting the pipes (& fittings) at wall/ceiling level supported by galvanized clamps, fastener, hangers etc, as per specification. Exposed pipes to be painted of legends with direction arrow. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Manager's / Consultant requirement.
1.1 | 1/2" dia (15 mm) | RM | 525
1.2 | 3/4" dia (20 mm) | RM | 60
1.3 | 1" dia (25 mm) | RM | 165
1.4 | 1.1/4" dia (32 mm) | RM | 350
1.5 | 1.1/2: dia (40 mm) | RM | 85
1.6 | 2" dia (50 mm) | RM | 160
1.7 | 2.1/2" dia (65 mm) | RM | 60
1.8 | 3" dia (80 mm) | RM | 178
1.9 | 4" dia (100 mm) | RM | 150
1.1 | 6" dia (150 mm) | RM | 0
Total Carried to Summary
2 | Providing and fixing nitrle rubber insulation on hot water supply / return pipes with Mechanical protection on nitrile rubber insulation as per manufacturers specification and approved by Project Manager / Consultnats.
2.1 | 1/2" dia (9 mm thickness) | RM | 525
2.2 | 3/4" mm dia (9 mm thickness) | RM | 60
2.3 | 1" mm dia (9 mm thickness) | RM | 165
2.4 | 1.1/4" mm dia (13 mm thickness) | RM | 350
2.5 | 1.1/2" mm dia (13 mm thickness) | RM | 85
2.6 | 2" mm dia (13 mm thickness) | RM | 160
2.7 | 2.1/2" mm dia (19 mm thickness) | RM | 60
2.8 | 3" mm dia (19 mm thickness) | RM | 178
2.9 | 4" mm dia (19 mm thickness) | RM | 150
2.1 | 6" mm dia (19 mm thickness) | RM | 0
3 | Providing and fixing male/ female screw ended full way lever operated forged brass ball valves with brass body with forged brass hard chrome plated ball / stem, union. Rated to temperature of 85 Deg C and tested to a pressure not less than 30 Kg/Sq.cm. Including covering with nitrile rubber insulation having protective coating against mechanical damage as per manufacturer’s specification (GI boxing to be provided).
3.1 | 15 mm dia | Nos. | 30
3.2 | 20 mm dia | Nos. | 160
3.3 | 25 mm dia | Nos. | 24
3.4 | 32 mm dia | Nos. | 40
3.5 | 40 mm dia | Nos. | 12
3.6 | 50 mm dia | Nos. | 10
4 | Providing and fixing C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated coated), Liner : HT - EPDM) of approved make with union / flange, washer, nuts & bolts. Rated to temperature of 85 Deg C and PN 10/16 pressure rating including nitrile rubber insulation with proprietary fire proof protective coating against mechanical damage as per manufacturer’s specification (GI boxing to be provided).
4.1 | 40 mm dia | No. | QR
4.2 | 50 mm dia | No. | QR
4.3 | 65 mm dia | Nos. | 4
4.4 | 80 mm dia | Nos. | 4
4.5 | 100 mm dia | Nos. | 8
4.6 | 150 mm dia | No. | QR
5 | Providing & fixing screw ended gun metal / Bronze horizontal/ vertical type non – return valve of approved make confirm IS : 778 class II with union / flange, washer, nuts & bolts. Rated to temperature of 85 Deg C and tested to a pressure not less than 30 Kg/Sq.cm. Including nitrile rubber insulation with proprietary fire proof protective coating against mechanical damage as per manufacturer’s specification.
5.1 | 15 mm dia | Nos. | 10
5.2 | 20 mm dia | Nos. | 160
5.3 | 25 mm dia | Nos. | 20
5.4 | 32 mm dia | Nos. | 10
5.5 | 40 mm dia | Nos. | 5
5.6 | 50 mm dia | Nos. | 10
6 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories testing to a pressure not less than 15 KG / sqcm including rubber gaskets, flanges nuts, bolts & washers complete as required.
6.1 | 50 mm dia | Nos. | 6
6.2 | 65 mm dia | Nos. | 4
6.3 | 80 mm dia | Nos. | 2
6.4 | 100 mm dia | Nos. | 4
7 | Providing and fixing auto air vent for Hot water supply system suitable for pressure not less than 15 Kg / Sqm.
7.1 | 15 mm dia | Nos. | 20
7.2 | 20 mm dia | Nos. | 2
8 | Making water supply connection to laundry / kitchen equipment, appliances etc., including necessary fittings, (pipes & valves to paid separately).
8.1 | Size 15 mm to 25 mm dia | Nos. | 12
8.2 | Size 32 mm to 50 mm dia | Nos. | 6
| Total Carried to Summary |  |  |  |  | 0
D | WATER TREATMENT PLANT
1 | Supplying, installing, testing and commissioning of SS-304 vertical/ horizontal multistage centrifugal filter feed pump. Each pump shall have TEFC 2900 RPM three phase electric motor. The pump shall have cast iron head, base plate SS Shaft/ Impeller/ Intermediate chamber. Pump shall be provided with mechanical seal. The pump shall be suitable for 415 + 10% volts, 3 phase AC supply, auto/ manual operation .
1.1 | Flow rate : 2.80 LPS (2 W+1S)
| Head : 25 Mts | No. | 3
Note: Pumps head shall be based on a hydraulic analysis of the system based on the final shop drawing and equipments selection.
2 | Supplying, installing, testing and commissioning of SHMP dosing system with ORP meter with controller consisting of one HDPE tank of 200 litres capacity with 1 nos. of positive displacement diphragm dosing pump having variable flow rate of 0-10 lph. ORP Meter cum controller variate the flow of dosing pump if the cholorine contents shall be above the limit including all necessary wiring and control etc. The motor shall be suitable for operation at 240 V / single phase /50 Hz. Supply. The pump shall be supplied complete with necessary polypropylene piping, valves, strainers, low level switch and injection fittings. The pump shall be speed & stroke control including necessary chemical etc. complete. | Set | 3
3 | Supplying, installing, testing and commissioning of FRP Filter vessel including, filter media Cpvc frontal piping schedule 40,multiport valve of 65 mm dia, all safety valves, and necessary accessories suitable for a flowrate of 4.5 LPS at 3.5 Kg/Sq cm pressure including filter media, etc. complete.
The material of construction shall be composite FRP.
3.1 | Dual Media Filter
Filteration velocity 9000 lts / hr / sq.m
| Filter dia – 1025 mm | Set | 1
4 | Supplying, installing, testing and commissioning of FRP Filter vessel including NSF certified birm iron/mn removal media of 900 mm bed depth, Cpvc frontal piping schedule 40,multiport valve of 65 mm dia, all safety valves, and necessary accessories suitable for a flowrate of 4.5 LPS at 3.5 Kg/Sq cm pressure etc. complete.
The material of construction shall be composite FRP.
4.1 | Iron Removal Filter
Filteration velocity 9000 lts / hr / sq.m
| Filter dia – 1020 mm | Set | 1
5 | Supplying, installing, testing and commissioning of FRP Filter vessel including filter media with frontal piping alongwith sall safety valves with 900 mm bed depth, Cpvc frontal piping schedule 40,multiport valve of 65 mm dia, all safety valves, and necessary accessories suitable for a flowrate of 4.5 LPS at 3.5 Kg/Sq cm pressure etc. complete.
The material of construction shall be composite FRP.
5.1 | Activated carbon Filter
Filteration velocity 9000 lts / hr / sq.m
| Filter dia – 1020 mm | Set | 1
6 | Supply, installation, testing & commissioning of the following instrumentation / controls complete with all accessories suitable for interface with BMS system.
7 | On-line mounted digital flow meter cum totalizer suitable for flow rate of 30-35cum/hr | Nos. | 2
8 | Supplying, installing, testing and commissioning of annunciation and indication panel with interlocking arrangement complete in accordance to specification with pressure switches, level controller (In fire water, raw water and treated water storage tanks : 6 Nos. level controller), level switch etc with control cabling from field to MCC as required. | Lot | 1
9 | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes and pumps supply and delivery header as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 40 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers,flanges, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.
Cost shall be inclusive of Fixing/supporting the pipes & fittings at wall/ceiling level supported by galvanized clamps, fastener, hangers etc, as per specification. Exposed pipes to be painted of legends with direction arrow. all as per Project Manager's / Consultant requirement.
9.1 | 2" dia (50 mm) | RM | QR
9.2 | 2.1/2" dia (65 mm) | RM | 100
9.3 | 3" dia (80 mm) | RM | 30
9.4 | 4" dia (100 mm) | RM | 50
10 | Providing & fixing butterfly valve (upto 150mm dia with hand lever operation). Rated for PN10 pressure rating. Including rubber gasket, flanges, nuts, bolts, washers & painting complete as required.
10.1 | 50 mm dia | No. | QR
10.2 | 65 mm dia | No. | 16
10.3 | 80 mm dia | No. | 2
10.4 | 100 mm dia | No. | 2
10.5 | 150 mm dia | No. | 6
11 | Providing & fixing gun metal horizontal flap type non return valve conforming to IS 778. Including rubber gasket, flanges, union, nuts, bolts & washers complete as required.
11.1 | 50 mm dia | No. | QR
11.2 | 65 mm dia | No. | 8
12 | Providing & fixing `Y' Strainer (screwed/ flanged) with stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required (on pump suction).
12.1 | 65 mm dia | No. | 8
12.2 | 80 mm dia | No. | 0
12.3 | 100 mm dia | No. | 1
13 | Providing and fixing in position of approved quality G.M. float valve with copper ball float and brass rods of required length suitable for pressure of 10 Kg/sqcm of the following sizes:
13.1 | 80 mm dia | No. | 2
14 | Providing and fixing 100 mm dia type pressure gauge with isolation valve complete | No. | 20
15 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories tested to a pressure not less than 15 Kg./sqcm including rubber gaskets, flanges, nuts, bolts & washers complete as required.
15.1 | 50 mm dia | No. | QR
15.2 | 65 mm dia | No. | 16
15.3 | 80 mm dia | No. | 2
15.4 | 100 mm dia | No. | QR
15.5 | 150 mm dia | No. | QR
B | HYDROPNEUMATIC SYSTEM
1 | HYDROPNEUMATIC SYSTEM (DOMESTIC WATER SUPPLY)
Supply, Installation, Testing And Commissioning of Compact Self Contained Hydropneumatic System As Follows:
1.1 a. | In-Line, Multistage, centrifugal pumps with SS-304 casing and impeller and SS-316 shaft, CI base & head TEFC motor (with mechanical seal)
(Vendor to submit performance curves and technical catalog of the proposed model for review & information)
The pump shall be selected for performance at best efficiency point. However, the pump selection shall be suitable for performance with set point @ + 20% of the rated head.
Nos. of Pumps : 3 Nos. (2 W + 1 SB)
Water Flow Rate : 7.5 LPS
Head : 75 M
b. | Providing and installation of External Pump mounted or wall mounted microprocessor PID controller and frequency inverter integrated in a single body or as separate components with pressure sensor transmitter minimum two lined LCD display, diodes to indicate pump ready, pump running and fault and capable to communicate with other controllers following MODBUS-RTU or BACNET Class-2 protocall through RS485 port. System should be capable to compensate for frictional losses at lower flows. All alarms should be displayed in the controller. System should be equiped with dry running protection
Quantity : 1 No.
c. | Precharged diaphram pressure vessel with food grade membrane, charging connection, connected to outlet header with necessary flanges, gaskets, isolating valves, nuts/bolts etc complete.
d. | Complete imported electrical control panel comprising of all set of accessories such as pressure switches, pressure transducers, inter connecting power and control cabling etc. complete as follows:
1.1.1 | Vertical Multistage Pump - 1 Set
1.1.2 | Variable Frequency Drive - 1 nos.
1.1.3 | Pressure Vessel (Capacity to be mentioned by Vendor) - 1 No.
1.1.4 | Providing and installation of Complete (Skid mounted wall mounted / floor mounted) electrical control panel comprising of all accessories such as PLCs, pressure switches, pressure transducers, control wiring and any other necessary imports etc. (list to be provided by the vendor). | Set | 1
C. | SUBMERSIABLE PUMPS
1 | Submersiable Centrifugal Non-clog Pumps.
Supply, installation, testing & commissioning of continuous duty submersible centrifugal non-clogging drainage pumps complete with 3 phase motor with all necessary protection and mechanical seal etc.
Vendor to submit proposed pump model with duty curve.
1.1.1 | Flow rate : 2 LPS
Head : 10 Mts
Solid Handling : 12 MM
Location : Sump of Plant room
Purpose : Plat room drainage
| MOC : CI Body. CI impeller & SS shaft | No. | 2
Note: | Shop drawing for the installation to be approved by the Project Manager prior to execution.
D | CONTROL PANEL
1 | Design, providing, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in cubicle in 3b formation with reinforcement of suitable size angle iron, channel ‘T’ sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadimium plated hardware shall be used in fabrication of panels.
1.2 | MCC – 1 (Water Treatment & Water Pumping)
Incoming
100 amps TPN MCCB with the following accessories:
a | 0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch shall be protected by 2 amps TP MCB. 1 Set
b | (0-100) amps 96 x 96 mm square digital electronic ammeter with selector switch and 60/5 amps 15 VA CL:1 CTs. 1 Set
c | Phase indicating lamps shall be protected by 2 amp SP MCB 3 Set
Bus Bar
150 amps TPN (25 KA) aluminium bus bar with heat shrinkable insulation sleeves.
Outgoings
a | 3 Nos. 16 amps TPN MCB for 3 nos. DOL starter of 1.5 KW and outgoing feeder to filter feed pump including 1 no. stand by pump. Each compartment shall contain direct ammeter of (0-20) amps range with auto/manual selector switch and indicating lamps with MCB’s and ‘ON/OFF/TRIP’ status of motor.
b | 3 nos. 16 amps DP MCB for dosing pumps.
c | 1 no. 16 amps DP MCB for UV units.
d | 2 nos. 63 amp TPN MCB's outgoing feeder to 2 set of Hydro-pneumatic water pumping system panels.
e | Spare MCB’s of following capacities:
32 amps TPN MCB 1 No.
20 amps TPN MCB 1 No.
f | Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also included.
Notes :
a | All MCCBs shall be of 25 KA & MCB’s of 10 KA breaking capacity and suitable for motor duty application.
b | All motor starter shall be provided with Automatic level controller.
c | Provision shall be made for providing potential free contacts to all pumps starters for connection to BAS.
| MCC - 1 (Water treatment & Water pumping system) described above | No. | 1
1.2 | MCC-2 CONTROL PANEL FOR RAIN WATER & PUMP ROOM DRAINAGE SUMP PUMP
Incoming
16 amps 4 pole MCB with the following accessories:
a | 0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch through 415 V/ Ö : 3 110 V/ Ö 3 PT primary and secondary of PT’s shall be protected by 2 amps TP MCB. 1 Set
b | 0-16 amps 96 x 96 mm square digital electronic ammeter with selector switch.
c | Phase indicating lamps shall be protected by 2 amp SP MCB 3 Sets
Bus Bar
25 amps TPN (10 KA) aluminium bus bar with heat shrinkable insulation sleeves.
Outgoing
a | 2 Nos. 10 amps 4 Pole MCB for 2 Nos. 1.5KW direct on line starter and outgoing feeders to rain water sump pumps. Each compartment shall contain direct operated digital electronic ammeter of 0-25 amps range with auto/manual selector switch and indicating lamps with MCB’s and ‘ON/OFF/TRIP’ status of motor.
b | Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also included.
Notes
a | All MCBs shall be of 10 KA breaking capacity and suitable for motor duty application.
b | All motor starter shall be provided with Automatic float type level controller.
c | Provision of high high level alarm shall also be made.
d | It shall be ensured that all pumps operate during high high level in the sump
e | Sequence timer for pump operation shall be provided
f | Provision shall be made for providing potential free contacts to all pumps starters for connection to BAS.
| Control Panel for Plant Room & Rain Water Sump Panel as described above | No. | 2
4 | CABLE & CABLE TRAYS
4.1 | Supplying & laying of following 1100 volt grade PVC sheathed copper conductor armoured cables as per specification in existing trenches, cable trays, ducts over bed of sand, clamped to wall with suitable clamps, saddles fixing bolts including connecting testing and commissioning.
a. | 3 core 25 sq. mm | RM | QR
b. | 3 core 16 sq. mm | RM | QR
c. | 3 core 10 sq. mm | RM | 30
d. | 3 core 6 sq. mm | RM | QR
e. | 3 core 4 sq. mm | RM | 50
4.2 | Supplying & laying of following 1100 volt grade PVC insulated copper conductor armoured cables as per specification in existing trenches, cable trays ducts over bed of sand, clamped to wall with suitable clamps, saddles fixing bolts including connecting testing and commissioning.
a. | 2 core 2.5 sq.mm control cable | RM | 30
b. | 4 core 2.5 sq.mm control cable | RM | 30
4.3 | Cable end termination of the following copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing facility and cable sockets etc. complete as required.
a. | 3 core 25 sq. mm. | No. | QR
b. | 3 core 16 sq. mm. | No. | QR
c. | 3 core 10 sq. mm | No. | 4
d. | 3 core 6 sq. mm | No. | QR
e. | 3 core 4 sq. mm | No. | 6
f. | 2 core 2.5 sq.mm control cable | No. | 10
g. | 4 core 2.5 sq.mm control cable | No. | 6
4.4 | Supply and fixing of perforated type GI cable trays with supports, hangers, fastners of the following sizes as per specification.
a. | 300 mm x 40 x 40 x 2 mm thick | RM | 20
b. | 150 mm x 25 x 25 x 2 mm thick | RM | 30
5 | EARTHING
5.1 | Supply and fixing of following bare copper tapes / wires including all necessary fixing accessories and effecting connections as per specifications.
a. | 25 x 3 mm thick Cu. tape. | RM | 20
b. | 3 MM Cu wire | RM | 50
TOTAL CARRIED TO SUMMARY
E. | INTERNAL DRAINAGE : (SOIL, WASTE & VENT)
1 | Providing, fixing, jointing, testing and commissioning UPVC soil & waste water pipe confirming to IS : 13592 or IS : 4985 or equivalent (Pipe Class III - 6 kg / sq.cm) cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. duly epoxy coated. Making proper connection with solvent cement as per manufacturar recomendations . Cutting, chases/holes in floors / walls / slab.
Providing fire retardent collar around pipe with the help of collar support, wherever pipes crossing a fire rated wall / floor slab and sealing of space around pipe at either end to the satisfaction of the Project Manager / Consultants and making good the same after pipes have been duly laid and testing complete
Cost shall also be inclusive of painting the pipes & fittings with two coats of synthetic enamel paint of approved shade over a coat of primer.
1.1 | 110 mm O.D | RM | 750
1.2 | 160 mm O.D | RM | 150
1.3 | 200 mm O.D | RM | 200
2 | Providing, fixing, jointing, testing and commissioning UPVC Rain water pipe confirming to IS : 4985 or equivalent (Pipe Class III - 6 kg / sq.cm) cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. duly epoxy coated. Making proper connection with solvent cement as per manufacturar recomendations . Cutting, chases/holes in floors / walls / slab.
2.1 | 110 mm O.D | RM | 0
2.2 | 160 mm O.D | RM | 100
2.3 | 200 mm O.D | RM | 250
2.4 | 250 mm O.D | RM | 150
3 | Providing, fixing, jointing, testing and commissioning of UPVC pipe (for Planter / landscape drain) confirming to IS : 13592, and confirming to IS : 4985 (Pipe Class III - 6 kg / sq.cm) cut to required lengths including all necessary fittings and specials such as bends, junctions offsets, access pieces (plain or door) & vent cowl. Fixing at wall / ceiling level supported by G.I. clamps, hangers etc. duly epoxy coated.
3.1 | 40 mm dia | RM | 200
3.2 | 50 mm dia | RM | 600
3.3 | 75 mm dia | RM | QR
3.4 | 90 mm dia | RM | QR
5 | Providing and fixing in position UPVC pipe and fittings 6kg/sqcm all complete set including Fittings as Bend Tee, Y-branch, vent cowl etc per specification and instruction. (for waste pipe from individual fixtures to floor trap / floor drain & vent pipe) Including fixing at wall / ceiling level supported by galvanized clamps and hangers etc., cutting chases in wall and filling with 1:1 cement mortar.
5.1 | 32 mm dia | RM | 150
5.2 | 40 mm dia | RM | 300
5.3 | 50 mm dia | RM | 450
5.4 | 65 mm dia | RM | 100
5.5 | 80 mm dia | RM | 100
6 | Providing and fixing in position Upvc full bore P / S trap of the following sizes for underslab location including providing necessary galvanized steel support and as per Specification and duly epoxy coated. Making proper connection with solvent cement, cutting chase / hole in floors / slabs and bringing the same in proper condition and shape after placing the trap in right position complete by supporting by GI clamps / hangers as required.
6.1 | 110 mm O.D inlet and 110 mm O.D outlet. | Nos. | 86
7 | Providing & fixing in position UPVC full bore P / S trap with 50 mm water seal of following sizes for embedded areas. Making proper connection with refined pig lead / drip seal joints, cutting chase / hole in floors /slabs and bringing the same in proper condition and shape after placing the trap in right position complete as required.
7.1 | 100 mm inlet and 100 mm outlet. | Nos. | 30
8 | Providing and fixing Heavy class SS grating with Cockroach proof SS strainer of approved design including setting in floor with cement motor to match with floor finish as per architect requirement & suitable for waste and FD.
8.1 | Size 100 mm x 100 mm or 100 mm dia | No. | QR
8.2 | Size 150 mm x 150 mm or 125 mm dia | No. | QR
9 | Providing and fixing of 304SS Gully, with grating which is screwed to the body of the gully, with removal Foul Air Trap(FAT),with telescopicadjustment & outlet dia of 75mm and height of 186mm, complete including necessary chasing / making hole in floor slab and making good complete as required. | Nos. | 150
10 | Providing and fixing Brass floor clean out plug comprising of GI pipe, socket, elbow, extension piece caulked to pipe and cast brass plug with suitable inlet key for opening male threaded joint with GI class C pipe & socket. Including lead / drip seal caulked to CI pipes or CI class LA pipes complete as required.
10.1 | For 75 mm dia pipe | No. | QR
10.2 | For 100 mm dia pipe | Nos. | 10
10.3 | For 150 mm dia pipe | Nos. | 0
10.4 | For 200 mm dia pipe | Nos. | 0
11 | Providing and fixing P.V.C. WC connector (straight or bend type) with rubber lip ring. Including 110 mm dia PVC pipe / bend of required length and proper connection with M seal to C.I. pipe complete as required | Nos. | 86
12 | Making drainage connection to kitchen / laundry equipment, appliances etc. including necessary GI pipes / fittings & Flexiable pipes complete as required.
12.1 | 32 mm dia to 50 mm dia | Nos. | 10
13 | Providing and fixing 25 mm thick CI grating with 30 x 30 x 5 mm angle frame with hold fasts welded at intervals of 600 mm with frame, setting with cement mortar 1:3 (1 cement : 3 sand) true to levels as required (for plant room). All M.S. Angles etc. must be hot dip galvanized.
13.1 | 300 mm wide x 600 mm length | Nos. | 12
13.2 | 200 mm wide x 600 mm length | No. | QR
14 | Providing & fixing rain water `Khurras' size 450x450 mm required depth with lead flashing around the pipe with one piece lead sheet of 3 mm thick set on a layer of cold bitumen. Including Heavy duty CI/MS grating as per drawing complete as required. | Nos. | 12
15 | Providing and fixing CI rain water head of required length with puddle flange to fix head in RCC slab including removable heavy duty dome type CI grating and CI hopper of approved design.
15.1 | 260 mm dia ; 110 mm outlet | No. | 6
15.2 | 400 mm dia; 160 mm outlet | No. | QR
15.3 | 400 mm dia; 200 mm outlet | No. | 32
16 | Providing and fixing CI manhole cover with frame.
16.1 | Medium duty double seal of 450 x 600 mm internal size and total weight of cover and frame to be not less than 50 Kg. | No. | 20
16.2 | Medium duty double seal of 600 x 600 mm internal size and total weight of cover and frame to be not less than 115 Kg. | No. | QR
Total Carried to Summary
F. | EXTERNAL SEWAGE / STORM WATER DRAINAGE:
1 | Providing, fixing, jointing and testing in position the following UPVC pipes confirming to IS:4985 of 6 Kg / Sq.cm for drainage system cut to required length. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil (hard rock), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification (For sewerage System).
1.1 | 110 mm dia | RM | QR
1.2 | 160 mm dia | RM | QR
1.3 | 200 mm dia | RM | 100
1.4 | 250 mm dia | RM | 80
2 | Providing and fixing stoneware gully trap of the following sizes in brick masonary chamber of standard design with first class bricks and trap to be set in cement concrete 1:2:4, both side 12mm thick plastering with floating coat of neat cement. Making necessary connections & providing water tight D.I. cover with frame of 300mm x 300mm internal size. The weight of cover & frame not be less than 8 kg as per standard design. Including necessary excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required.
2.1 | 300 x 300mm chamber with 150 x 100mm size `P' trap | Nos. | 6
2.2 | 450 x 450mm chamber with 150 x 150mm size `P' trap | Nos. | QR
3 | Designing , providing and constructing brick masonry inspection chamber of the following sizes in brick work of class 75 in cement mortar 1:5 (1 cement:5 fine sand), R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm. nominal size) embeded with frame for manhole, RCC foundation slab. 1:2:4 mix (1 cement : 2 coarse sand:4 graded stone aggregate 40 mm nominal size) both inside and outside of plastering 12 mm thick with cement motar 1:3 (1 cement : 3 coarse sand) with a floating coat of neat cement on inside face, proper water proofing to ensure no ground water seepage in the manhole, Poly propylene (conforming to ASTMD - 4101) foot rests (meeting the 224 kg load requirement as per IS 5455) at 300 mm spacing, benching and making channels with 1:2:4 cement concrete neatly finished, including necessary centering and shuttering, reinforcement, excavation, in all kind of soil, dewatering, refilling, watering, ramming and removing the surplus excavated earth, making good the same complete as required. for storm water & sewerage system
Contractor shall submit the structural design and drawings for the approval of Project Manager prior to execution.
3.1 | 600 x 800 x 600 mm size | No. | 4
3.2 | 900 x 800 x 600 mm size | No. | 6
3.3 | 1200 x 900 x 900 mm size | No. | 3
3.4 | 900 mm dia size and 1200 mm deep | No. | 2
4 | Providing & fixing SFRC Manhole cover with frame:
4.1 | For 600 x 800 mm MH
4.2 | 450 X 450 mm, Medium Duty (Wt minimum 58 kg, cover with frame) | No. | QR
4.3 | 450 X 600 mm, Medium Duty (Wt minimum 102 kg, cover with frame) | No. | 4
4.4 | For 900 x 800 mm MH
4.5 | 600 X 600 mm, Medium Duty (Wt minimum 140 kg, cover with frame) | No. | QR
4.6 | 560 dia Medium Duty (Wt minimum 101 kg, cover with frame) | No. | 6
4.7 | For 1200 x 900 mm, 900 & 1500 mm dia MH
4.7.1 | 560/ 600 mm dia Heavy Duty (Wt minimum 180 kg, cover with frame) | No. | 3
4.7.2 | 560/ 600 mm dia Extra Heavy Duty (Wt minimum 228 kg, cover with frame) | No. | 2
| Total Carried to Summary |  |  |  |  | 0
| TOTAL FOR SANITARY AND PLUMBING WORKS |  |  |  |  | 0
FIRE FIGHTING SYSTEM
A | ELECTRICAL INSTALLATION FOR FIRE PROTECTION SYSTEM
1 | Providing and installation of MCC-1 for Fire Protection equipments
a | One No. 400 amps TPN incoming MCCB complete with the following:
i | 0-500 volts 96 x 96mm square voltmeter with selector switch shall be protected by 2 amps TP MCB
1 Set
ii | 0-400 amps 96 x 96 mm square ammeter with 400/5 amps 15 VA CL:1 CT's and selector switch
1 Set
iii | Phase indicating lamps shall be protected by 2 amps SP MCB
3 Sets
b | Aluminium bus bar sleeves type, rated at 600 amps for three phase & neutral phase bus bar shall have maximum current density of 1 amps per sq.cm. and the neutral bus bar of not less than 50% capacity.
Outgoing :
c | 2 Nos. 250 amps TPN MCCB outgoing feeders with 75 KW DOL starters out going feeders to Hydrant / Sprinkler pump motor. The compartment shall contain CT operated ammeter of 0-250 amps range with selector switch, auto / manual selector switch and indicating lamp with MCBs for `ON'/OFF` status of motor.
d | 2 Nos. 32 amps TPN MCCB, 7.5 KW Direct online starter with single phase preventer and outgoing feeder to jockey pump motor. The compartment shall contain CT operated ammeter of 0-30 amps and indicating lamps with MCBs for `ON'/OFF`TRIP' status of pump motors.
e | Providing and fixing 1 No. auto start panel activated with pressure switch for diesel engine complete with all accessories, batteries, battery charger of suitable rating, MCB timers, push buttons, microprocessor based alarm annunciator, wiring and cabling including connection to diesel engine complete as required ready for working.
f | Necessary cable alleys space for spare switches, internal wiring and copper earthing of all equipment shall also be included. All switch gears/control gears shall be motor duty rating.
Note:
All MCCB's to be suitable for motor duty and shall be of 35 KA breaking capacity.
Provision shall be made for providing potential free contacts to all pumps starters for connection to building automation system.
| MCC-1 as described above | Set | 2
2 | CABLE & CABLE TRAYS
2.1 | Supplying & laying of following 1100 volt grade PVC sheathed aluminum copper conductor armoured cables as per specification in existing trenches, cable trays, ducts over bed of sand, clamped to wall with suitable clamps, saddles fixing bolts including connecting testing and commissioning.
2.1.1 | 3.5 core 120 sq.mm aluminium cable | RM | 50
2.1.2 | 3 core 6 sq. mm copper cable | RM | 55
2.1.3 | 3 core 4 sq. mm | RM | 35
2.2 | Supplying & laying of following 1100 volt grade PVC insulated copper conductor armoured cables as per specification in existing trenches, cable trays ducts over bed of sand, clamped to wall with suitable clamps, saddles fixing bolts including connecting testing and commissioning.
2.2.1 | 2 core 2.5 sq.mm control cable | RM | 40
2.2.2 | 4 core 2.5 sq.mm control cable | RM | 25
2.3. | Cable end termination of the following copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing facility and cable sockets etc. complete as required.
2.3.1 | 3.5 core 120 sq.mm | Nos. | 8
2.3.2 | 3 core 6 sq. mm | Nos. | 8
2.3.3 | 3 core 4 sq.mm | Nos. | 8
2.3.4 | 2 core 2.5 sq.mm control cable | Nos. | 10
2.3.5 | 4 core 2.5 sq.mm control cable | Nos. | 6
2.4. | Supply and fixing of perforated type GI cable trays with supports, hangers, fastners of the following sizes as per specification.
2.4.1 | 300 mm x 40 x 40 x 2 mm thick | RM | 20
2.4.2 | 150 mm x 25 x 25 x 2 mm thick | RM | 35
3 | EARTHING
Supply and fixing of following bare copper tapes / wires including all necessary fixing accessories and effecting connections as per specifications.
3.1 | 25 x 6 mm thick GI strip. | RM | 30
3.2 | 8 SWG GI wire | RM | 65
| Total Carried to Summary |  |  |  |  | 0
B | FIRE PROTECTION SYSTEM:
1 | Fire Pump & Equipment:
1.1 | Supply, installation, testing and commissioning of electrically driven high pressure centrifugal fire hydrant / sprinkler pump, suitable for automatic operation consisting of the following:
a. | Horizontal end suction / high pressure single / multistage, centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and S.S. (304) Shaft with mechanical seal, capable for delivering 2250 LPM at outlet head of 70 mts to ensure a minimum pressure of 3.5 Kg/Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side, necessary MS base frame (epoxy coated after fabrication), anti vibration mounting arrangement including supply of bolts, nuts, fastners etc., effecting proper connections, anchoring, grouting testing and commissioning above equipment all complete as required.. (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority).
Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head.
b. | Squirrel cage induction motor, TEFC type suitable for operation on 415 volts, 3 phase 50 HZ A.C supply, for the above pump with synchronous speed of 2900 RPM, conforming to IP 55 protection & class F insulation. The motor shall conform to IS 325-1978 (up to date) with flexible coupling and coupling guard, complete as required.
c. | Common base plate for (a) and (b) from M.S. Channel for required size.
d. | Suitable cement concrete foundation with cement concrete plaster (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with anti-vibration arrangement of cushy foot mountings. | Set | 2
1.2 | Supply, installation, testing and commissioning of jockey pump (pressurisation pump) comprising of the following:
a. | Vertical Multistage centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with Flexible coupling and coupling guard, complete as required. Jockey pump shall be of stainless steel construction.
The pump head and base shall be CI construction and impellers, diffusers, shaft sleeve, seal bush & pump shaft shall be in SS 304 material. The pump shall be provided with mechanical seal The system shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side, necessary MS base frame (epoxy coated after fabrication), anti vibration mounting arrangement including supply of bolts, nuts, fastners etc., effecting proper connections, anchoring, grouting testing and commissioning above equipment all complete as required. (The pump should meet the condition and shall be gotten approved by the Local fire Authority).
b. | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with a synchronous speed of 2900 R.P.M. with flexible coupling and coupling guard etc. as required.
c. | Common base plate for (a) and (b) from M.S. channel as required size.
d. | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with Antivibration arrangement of cushy foot mounting.
For pump defined above & of duty as follows :
1.3.1 | Hydrant System
Flow : 180 LPM
| Head : 88 mts | Set | 1
1.4 | Providing, fixing, testing and commissioning of precharged air vessel (size 450 mm dia & 2000 mm height) for pressurization of hydrant / sprinkler system complete with adequate pressure switches (as per design / requirement) with valves to operate as per operating sequences including 25 mm dia drain valve, air release valve with stop cock on the top, minimum 50 mm dia inlet with isolating valve duly painted from inside and outside with two coats of synthetic enamel paint over a coat of primer complete as required. (Vessel should be suitable for rated working pressure).in pump room | Set | 1
1.5 | Providing, fixing, testing & commissioning of MS air cushion tank on top of each riser fabricated from 6mm thick MS plate, 200 mm in diameter and 1.2 m in height with dished ends fabricated from 6 mm thick MS plate with Air release valve & stop cock, flanged inlet connection with all accessories as required and conforming to IS 4736-1968. (The cushion tank should be suitable for rated working pressure. at top of riser | Set | 1
1.6 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI. Cost shall be inclusive of providing any short pieces, nipples, elbows etc as required. | Nos | 6
1.7 | Supply, installation, testing and commissioning of sight tube (of 3.5 to 4 m length) with isolation valve at top / bottom, demarcation on tube for making the installation of level indication on the RCC water tank complete. | Nos | 1
Note : | Contractor shall include in his rates for providing level controllers, pressure switches, wiring, cabling from level controller / pressure switch to panel etc. complete as required to operate the system automatic/manual. Pump shall be protected against running dry.
2 | Hydrants, Piping & Accessories:
2.1 | Providing, laying, jointing, testing and commissioning of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. MS pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head.. Welding of any kind on the galvanized support / hanger shall not be permitted.
For wet riser System - GI `C' Heavy class pipe
2.1.1 | 80 mm dia | RM | 100
2.1.2 | 100 mm dia | RM | 200
2.2 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager
2.2.1 | 80 mm dia | RM | 100
2.2.2 | 100 mm dia | RM | 200
2.3 | Providing protection to embedded MS/ GI pipes and fittings by applying protective primer (@ 100 gm/sqm) thereafter wrapping 4 mm thick protection coating by thermo fusion process. Overlap shall be maintained at 15 mm. The application process shall be strictly according to manufacturer’s specification.
2.3.1 | 80 mm dia | RM | 100
2.3.2 | 100 mm dia | RM | 50
2.3.3 | 150 mm dia | RM | 600
2.4 | Providing and fixing forged brass ball valve with forged brass ball (suitable for test pressure of not less than 30 kg / sq.cm of the following size : at riser drain and pump by pass line
(Cost shall be inclusive of providing necessary union / flange connection).
2.4.1 | 25 mm dia | No. | 2
2.4.2 | 32 mm dia | No. | 2
2.4.3 | 40 mm dia | No. | 4
2.4.4 | 50 mm dia | No. | 5
2.5 | Providing & fixing of butterfly valve (PN 16) with flanges, nut bolts, gaskets and necessary pad locking arrangement complete required.
2.5.1 | 50 mm dia | No | 2
2.5.2 | 65 mm dia | No. | 2
2.5.3 | 80 mm dia | No. | 10
2.5.4 | 100 mm dia | No. | 16
2.5.5 | 150 mm dia | No. | 6
2.5.6 | 150 mm dia (with electrical gear box operation) | No. | QR
2.5.7 | 200 mm dia (with electrical gear box operation) | No. | 6
2.5.8 | 250 mm dia (with electrical gear box operation) | No. | 3
2.5.9 | 300 mm dia (with electrical gear box operation) | No | QR
2.6 | Providing and fixing tamper switch on butterfly valve / sluice valve / isolation valve for remote mointing of the valve open / close position. The tamper switch shall be provided with potential free contact with 2 nos. NONC. The valve shall also be provided with manual lock & chain arrangement. | Set | 40
2.7 | Providing & fixing C.I. wafer type check valve of rating PN 16 rating including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required.
2.7.1 | 50 mm dia | No | QR
2.7.2 | 65 mm dia | No | 2
2.7.3 | 80 mm dia | No. | QR
2.7.4 | 100 mm dia | No. | QR
2.7.5 | 150 mm dia | No. | 2
2.7.6 | 250 mm dia | No. | 1
2.8 | Providing & fixing of CI /forged brass body gate valves confirming to IS:778 class II with high tensile brass rising stem suitable for the system pressure 10 kg/ cm2 including & fitting etc complete as required.
2.8.1 | 25 mm dia | No. | 2
2.8.2 | 32 mm dia | No. | 5
2.8.3 | 40 mm dia | No. | 4
2.8.4 | 50 mm dia | No. | 6
2.8.5 | 65 mm dia | No. | 2
2.8.6 | 80 mm dia | No. | 2
2.9 | Providing, fixing and commissioning of spring loaded relief valve suitable for pressure of 15 Kg / sq.cm including flanges, nuts, bolts, washers etc. complete as required.
2.9.1 | 80 mm dia | No. | 2
2.1 | Providing & fixing heavy duty double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per manufacturers specs including rubber gaskets, flanges, nuts, bolts and washers complete as required.(at pump suction at discherge side)
2.10.1 | 50 mm dia | No. | QR
2.10.2 | 65 mm dia | No. | 4
2.10.3 | 80 mm dia | No. | 4
2.10.4 | 100 mm dia | No. | QR
2.10.5 | 150 mm dia | No. | 6
2.10.6 | 200 mm dia | No. | 6
2.11 | Providing and fixing C.I.`Y' strainer with bronze perforated sheet basket including rubber gasket, flanges, nuts, bolts and washers, complete as required.(at pump suction header)
2.11.1 | 65 mm dia | No. | QR
2.11.2 | 80 mm dia | No. | 2
2.11.3 | 100 mm dia | No. | QR
2.11.4 | 150 mm dia | No. | QR
2.11.5 | 200 mm dia | No. | 2
2.11.6 | 250 mm dia | No. | QR
2.12 | Providing & fixing pot strainer fabricated out of 8 mm thick MS plate having 18 gauge SS basket (with 3 mm perfoation) and SS handle. The basket shall be supported at bottom so as to stand weight of water on solid brass blocks.
2.12.1 | 300 mm dia | No. | QR
2.13 | Providing and Fixing non rising sprindle type sluice valve PN 16 rating of following dia complete with flanges, nuts, bolts etc.(external hydrant line)
2.13.1 | 100 mm dia | Nos. | QR
2.13.2 | 150 mm dia | Nos. | 2
2.13.3 | 200 mm dia | Nos. | QR
2.14 | Providing & fixing gun metal fire hydrant single landing valve with 80 mm N.B. flanged inlet, brass spindle controlled 63 mm dia female instantaneous outlet type. G.M. coupling, blank cap, chain, twist release type lug & all accessories Conforming to IS:5290. Including fixing with anchor fastner and flanged tapping from wet riser and providing pressure gauge with gun metal ball valve complete as required. | Nos. | 10
2.15 | Providing & fixing gun metal controlled pressure hydrant valve (Class 'F' Hose pressure regulator) with 2 1/2 " instantaneous female coupling to BS: 336. Inlet pressure range 4.8 to 20.7 bar; outlet pressure range 4.1 - 8.3 bar. The pressure regulator shall incorporate spring loaded balanced PRV combined with a hydrant slop valve. Cost shall be inclusive of fixing with anchor fastner and flanged tapping from wet riser and providing pressure gauge with gun metal ball valve complete as required. | Nos. | 10
2.16 | Providing & fixing swinging type First Aid hose reel in red colour drum with 36 mts long and 20 mm dia heavy duty rubber water hose, 20 mm dia gate valve stop cock, (IS:778, class - II) terminating with G.M. coupling & nozzle of 6mm outlet with shut off valve confirming to IS 8090 - 1976 complete with MS socket for tap-off, drum and brackets (including painting) for fixing on wall with anchor fastner, bolts & nuts conforming to IS:884-1985 (Reaffirmed 2000) complete as required. | No. | 10
2.17 | Providing & fixing non-percolating rubber reinforced lined fire hose pipe (as per IS : 636) type-B of 63 mm dia and length as described below. The hose shall be rated for brust pressure of 35.7 Kg/sqcm. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & rivetted to hose pipe with copper rivets & 1.5 mm copper wire (Location : Internal fire hydrant)
2.17.1 | 7.5 m length | Nos
2.17.2 | 15 m length | Nos. | 10
2.18 | Providing & fixing controlled percolation fire hose pipe (as per IS:8423) of 63 mm dia and 15 meter length rated for brust pressure of 35.7 Kg/sqcm. The hose shall be tested for flame resistance test in accordance to IS:8423. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & riveted to hose pipe with copper rivets & 1.5 mm copper wire (Location : External fire hydrant) | Nos. | 10
2.19 | Providing and Fixing 63 mm dia instantaneous pattern branch short gunmetal pipe, 20 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. | Nos. | 10
2.2 | Providing and fixing standard firemans axe with heavy rubber handle. | Nos. | 10
2.21 | Providing and fixing weather proof lockable cabinet of size not less than 0.9 x 0.6 x 0.45 mtr made out of SS304 sheet of 16 gauge thickness having central opening and 4 mm thick glazed glass doors (Two nos.) suitably marked on the outside with the letters "FIRE HOSE" including necessary locking arrangement and shall be painted with one coat of primer and two coats of synthetic enamel paint of approved shade.
The cabinet shall be suitable to accommodate 2 nos. 15 mtr long Hose pipe & 1 Nos branch pipe nozzle. It shall be mounted on raised Brick platform complete as required.
| (Cost shall be inclusive of providing break glass box containing key for the cabinet along with hammer). | Nos. | 6
2.22 | Providing & fixing lockable indoor type fire hose cabinet frames fabricated from 40 x 40 x 5 angle iron sections and 16 gauge MS sheet with full front glass door and locking arrangement, suitable to accommodate landing valves, 2 nos. 15 m long hoses, first-aid hose reel and branch pipe nozzle & fire mans’ axe. The cabinet frame shall be painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade of as required (Approx 2.1 m (high) x 0.9 m (wide) x 0.6 m (deep) ). The item shall be complete of MS housing with front door.(external finish as/ I.D)
| (Cost shall be inclusive of providing break glass box containing key for the cabinet along with hammer). | Nos. | QR
2.23 | Providing & fixing gun-metal fire brigade inlet connection (suction collecting head) consisting of 4 Nos. 63 mm dia instantaneous type male couplings with built-in check valves, 1 No. 150 mm dia sluice valve, and 150 mm dia flanged outlet complete with bolts, nuts and rubber insertions as required and as per IS:904-1963. | Nos. | 2
2.24 | Providing & fixing SS cabinet (to enclose above FB connection) fabricated from 16g SS 304 sheet with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry platform as required (Approx 0.6m x 0.6m x 0.45m) | Nos. | 2
2.25 | Providing & fixing gun-metal fire brigade suction hose coupling (draw-out connection) with nut for female coupling as per IS: 902-1992 (Reaffirmed 2007) complete with 100 mm dia GI suction pipe and 100 mm dia foot valve (to be connected to static tank). Provision of GI drop pipe and foot valve shall be made in all the fire water static storage tanks (2 Nos) (GI pipe to be paid separately through appropriate item while cost of foot valve to be included). | Set | 1
2.26 | Providing & fixing SS cabinet (to enclose draw-out connection as per Item above) fabricated from 16 g SS 304 sheet with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry paltform as required (Approx 0.6 m x 0.6 m x 0.45 m) | Nos. | 1
2.27 | Providing and fixing 5 mm thick glass door (with M.S. frame) of size 2.1 m x 0.9 m with center opening for fire hose cabinet. Suitably marked on the outside with the letters "FIRE HOSE" including locking arrangement. All M.S. work to be in Red P.O. colour over appropriate primer. The above item is only for masonary fire station.(finish as per I.D) | No. | 10
2.28 | Providing and fixing 4 mm thick glass door of size 2.1 m x 0.9 m along with anodised aluminium frame with centre opening for fire hose cabinet. Suitably marked on the outside with the letters FIRE HOSE including locking arrangement. Complete door & frame work to be in Red P.O. color over a coat of primer. | No. | QR
2.29 | Providing and fixing heavy class GI / MS suction & delivery headers of required length conforming to IS:3589 with welded joints standard MS Fittings and with end flange connections having inlet & outlet flanged connections including GI supports from wall/ floors & ceiling complete as required. Cost should be inclusive of all supports / clamps / brackets, anchor fastner etc. as required (all in GI). Pipes upto 200 mm dia shall be GI & above 200 mm shall be M.S.(In pump room)
2.29.1 | 65 mm dia (C Class) | RM | 20
2.29.2 | 80 mm dia (C Class) | RM | 15
2.29.3 | 100 mm dia (C Class) | RM | 5
2.29.4 | 150 mm dia (C Class) | RM | 30
2.29.5 | 200 mm dia (6 mm thick) | RM | 30
2.3 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager
2.30.1 | 65 mm dia | RM | 20
2.30.2 | 80 mm dia | RM | 15
2.30.3 | 100 mm dia | RM | 5
2.30.4 | 150 mm dia | RM | 30
2.30.5 | 200 mm dia | RM | 30
2.30.6 | 250 mm dia | RM | 40
2.30.7 | 300 mm dia | RM | 20
2.31 | Providing and Constructing brick masonary chamber (for housing sluce valve) in brick work with bricks of class 75 in cement mortar 1:5 (1 cement:5 fine sand) 12 mm thick plaster on inside with a floating coat of neat cement &rough plaster on external faces with cement mortar 1:3 (1 cement : 3 coarse sand) with 150 mm thick PCC (1:4:8). Including providing 100 mm thick R.C.C. top slab complete in all respect. Cost shall be inclusive of excavation in earth, shoring, dewatering, support to valve and access rungs as required to complete the work.
2.31.1 | Size 1200 x 900 x 1000 mm deep | No. | 1
2.32 | Providing & fixing SFRC Heavy duty manhole cover with frame of 560 mm internal dia for valve chamber (total weight of cover and frame to be not less than 157 kg ).at man hole & water tank | No. | 4
2.33 | Providing and laying Cement concrete for anchor / thrust blocks of 1:2:4 [1 cement : 2 fine aggregate : 4 coarse aggregate, 40 mm nomional size as per standard design. | Cum | 2
2.34 | Providing & fixing brass/ SS mosquito proof grating in elbow with necessary GI vent pipe with fittings (at water tank) | Nos. | 2
2.35 | Providing & fixing mosquito proof brass/ SS overflow grating for tanks | Nos. | 2
2.36 | Supply, installation, testing and commissioning of long range 360 deg. rotation monitor complete with stand pipe and standard accessories. | Nos. | QR
3 | Sprinkler, Piping & Accessories:
3.1 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings ( all pipes & fittings upto 50mm dia threaded shall be the threaded Ductile Iron (ASTM A536) or Cast Iron (ASTM A126) or Forged Steel fittings and for pipes above 50 mm dia MS fitting with welded joint shall be used) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on wall /ceiling with clamps, hangers (using anchor fastners) as per specification.
MS pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted.
For Sprinkler system - MS `C' Heavy class pipe
3.1.1 | 25 mm dia | RM | 1800
3.1.2 | 32 mm dia | RM | 250
3.1.3 | 40 mm dia | RM | 185
3.1.4 | 50 mm dia | RM | 200
3.1.5 | 65 mm dia | RM | 150
3.1.6 | 80 mm dia | RM | 65
3.1.7 | 100 mm dia | RM | 182
3.1.8 | 150 mm dia | RM | 100
3.2 | Providing, fixing, jointing and testing in position the for drainage purpose following medium class (Class B) G.I. pipes conforming to IS:1239 cut to required lengths including all necessary fittings (All fittings shall confirm to IS:1879 (part 1 to 10) and specials such as bends, tees, unions, Reducers, flanges & plugs etc. fixing at wall / ceiling level supported by clamps, hangers (using anchor fastners) etc, as per specification. Threading, jointing, and making proper connections, cutting hole in wall / floor / slab and making good the same. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealent compound at either end all as per Project Manager's / Consultant requirement.
All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted.
3.2.1 | 25 mm dia | RM | 50
3.2.2 | 50 mm dia | RM | 50
3.2.3 | 65 mm dia | RM | 25
3.2.4 | 80 mm dia | RM | 265
3.2.5 | 100 mm dia | RM | QR
3.2.6 | Providing & fixing Auto Air vent for cold water supply risers, suitable for pressure not less than 15 Kg/Sq.cm. | No. | 4
3.3 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager
3.3.1 | 25 mm dia | RM | 1800
3.3.2 | 32 mm dia | RM | 250
3.3.3 | 40 mm dia | RM | 185
3.3.4 | 50 mm dia | RM | 200
3.3.6 | 65 mm dia | RM | 150
3.3.7 | 80 mm dia | RM | 65
3.3.8 | 100 mm dia | RM | 182
3.3.9 | 150 mm dia | RM | 100
3.4 | Providing & fixing of butterfly valve of PN 16 rating with flanges, nut bolts & gaskets complete required. Butterfly valve shall be with pad locking arrangement.
3.4.1 | 50 mm dia | No. | QR
3.4.2 | 65 mm dia | No. | QR
3.4.3 | 80 mm dia | No. | QR
3.4.4 | 100 mm dia | No. | 2
3.4.5 | 150 mm dia | No. | 22
3.4.6 | 200 mm dia (with gear box operation) | No. | 2
3.4.7 | 250 mm dia (with gear box operation) | No. | QR
3.5 | Providing & Fixing of Installation Control Valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve and all other necessary components as per manufacturer's specifications complete as required.
3.5.1 | 100 mm dia | No. | QR
3.5.2 | 150 mm dia | No. | QR
3.6 | Providing and fixing installation control valve as above but excluding alarm gong.
3.6.1 | 150 mm dia | No. | 4
3.7 | Providing & fixing brass quartzoid sprinklers (UL listed) of 15 mm dia size, suitable for sustaining the pressure on the seat & water hammer effect. The type & temperature rating shall be as follows :
3.7.1 | Pendent/ upright type (68) deg.C) sprinkler. | Nos. | 584
3.7.2 | Pendent / upright (79 deg. C) sprinkler for non A/c areas. | Nos. | 20
3.7.3 | Pendent / upright (93 deg.C) sprinkler for kitchen & laundry | Nos. | 30
Note: i. | All sprinkler shall be chrome finish / powder coated except for the concealed ones. The concealed sprinkler shall be of brass finish. The cover plates of the concealed sprinkler shall be factory painted at manufacturer’s work and the shade shall be confirmed prior to application on the cover plate.
ii. | The sprinkler shall be either pendent OR upright type and shall not be universal style / nature.
iii. | Contractor shall ensure provision of sprinkler guard at no additional cost, as required by the Project Manager.
iv. | Shop drawing for multi spray sprinkler system shall be submitted for comment / approval to the owner / project manager /consultant.
4 | Providing, fixing, testing & commissioning of U.L.listed/ FM approved corrugated SS-304 Braided flexible sprinkler pipe droplet for 12 kg/ sq. cm. working pressure with 1/2" BSP threaded outlet & 1" BSP threaded inlet with reducer nipple, snap, clamp, T-bar bracket etc. with necessary fitting complete as required.
4.1 | 1000 mm length | Nos. | 350
Note : | Cost shall be inclusive for approval of fire hydrant & sprinkler system from local fire authority and any other relevant statutory authority at initial & various other stages of works, including preparation of report / drawings as per fire authority. Contractor shall include cost of all liaison works which are not explicitly mentioned above but are mandatory to have fire authority approval (any statutory charges will be reimbursed as per actual upon production of the invoice / challan).
5 | Portable Chemical Fire Extinguishers:
Supply, installation, testing and commissioning of following types of extinguisher with provision of wall bracket (fixed with anchor fastner).
5.1 | ISI marked (IS:940) portable fire extinguisher, water (gas pressure) type capacity 9 litres with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets | Each | 80
5..2 | 22.5 kg capacity (trolly mounted) | Each | 2
6 | ISI marked (IS:2171) Portable Dry Chemical Power Type Fire Extinguisher with Gun Metal cap and nozzle complete in all respects including initial fill of power and wall suspension bracket
6.1 | 2 Kg | Each | QR
6.2 | 5 Kg | Each | 25
7 | Ffully charged ABC (Powder Type) Fire Extinguisher. In HP Mild Steel Cylinders ISI marked/ TAC approved fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and confoming to IS:1349-1993
7.1 | 2 Kg | Each | 10
7.2 | 5 Kg | Each | 8
7.3 | 10 Kg | Each | 2
8 | Supplying and installing at approved location approved make fire buckets of 24 gauge galvanized steel sheet, standard 9 litre capacity and of round bottom shape, painted white inside and red outside and black on the bottom, inscribed with letters “FIRE” in black and gold. Cost shall be inclusive of providing MS stand duly painted over a coat of primer. | Nos. | 12
| Total Carried to Summary |  |  |  |  | 0
| TOTAL FOR FIRE FIGHTING SYSTEM |  |  |  |  | 0
HVAC SYSTEM
A. | VARIABLE REFRIGERATNT FLOW (VRF/VRV) SYSTEM
1.1 | Supply Installation, testing and commissioning of Modulating outdoor units must be equipped inverter / equivalent technology driven and highly efficient, with multi scroll compressors (minimum two compressors) with one capacity controlling compressor and other constant speed type compressor, special pre-coated fins, panel, corrosion resistant (suitable for seaside installation) coated condenser, inverter based condenser fan M.S. hot dip galvanised stands / supports, electrical & microprocessor panel, isolating valves and all the necessary accessories for proper functioning of the units, having following approximate capacities. The compressor should be heat pump type with heating and cooling available.
Note : Fins and copper tubes of Air Cooled Condenser along with copper tubing / piping with all joints and U-Bends exposed to coastal areas corrosive atmosphere / aggressive ambient, shall be painted with special orrosion prevention coating either in factory or at site.
1.1.1 | Outdoor Unit Cooling and Heating Capacity as listed below
a. | Cooling Capacity: 45.0 KW and Heating Capacity:50.0 KW | Nos. | 11
1.2 | Supply installation, testing and commissioning of VRF based indoor units complete with remote and all accessories, Vibration isolators & supports.
1.2.1 | Cassette type having following approximate Cooling Capacities.
a. | 5.6 KW | Nos. | 2
b. | 4.5 KW | Nos. | 2
c. | 3.6 KW | Nos. | 6
d. | 2.8 KW | Nos. | 18
e. | 2.2 KW | Nos. | 11
1.2.2 | Ductable type Unit having following approximate capacities.
a. | 28 KW With High Static Pressure machine. | Nos. | 7
b. | 19.3 KW With High Static Pressure machine. | Nos. | 2
c. | 14.0 KW With High Static Pressure machine. | Nos. | 2
d. | 4.5 KW | Nos. | 5
e. | 3.6 KW | Nos. | 66
f. | 2.8 KW | Nos. | 2
1.3 | Indicate for all port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | Nos. | 120 | Included above
1.4 | Customs duty and countervailing duty for the above imported equipment. | Nos. | 120 | Included above
1.5 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | Nos. | 120 | Included above
1.6 | Supply installation, testing and commissioning of Computer controlled network system for monitoring & controlling all indoor & outdoor units, central point including all software & cabling (I-manager) / I. Touch central controller. | Lot | 1 | Included above
1.7 | Supply installation , testing commissioning of All refrigerant joints. | Lot | 1 | Included above
1.8 | Indicate for all port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | Nos. | 120 | Included above
1.9 | Customs duty and countervailing duty for the above imported equipment. | Nos. | 120 | Included above
1.1 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | Nos. | 120 | Included above
1.11 | All refrigerant piping along with insulation and supports, between indoor & outdoor units duly insulated as per specifications. All piping inside the room shall be properly supported with hanger and exposed piping shall be properly supported in cable tray | Lot | 1 | Included above
1.12 | Drain piping with 6mm nitrile rubber insulation from indoor unit to nearest drain point. Drain piping shall be C-PVC. Piping shall be complete with supports. | Lot | 1
1.13 | Power cabling & earthing as per specifications between out door unit & indoor units. Power supply 3 phase 415 Volts will be made available near outdoor units Contractor to provide panel for onward power / control supply to outdoor units, single phase power / control supply to indoor units alongwith power / control cabling, supports trays etc. | Lot | 1 | Included above
| Sub Total Carried to Summary |  |  |  |  | 0
2 | Supplying, installing, testing and commissioning of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper.
The fan shall have low sound level exceeding not more than 40 DBA at three metre distance.
Sr.no Fan Tag CFM SP Motor (mmwg) (KW)
2.1 | 1 Inline Fan 800 25 0.75 | Nos. | 9
2.2 | 1 Inline Fan 1200 25 0.75 | No. | 3
2.3 | 1 Inline Fan 2000 25 1.1 | Nos. | 2
2.4 | 1 Inline Fan 2500 25 1.1 | No. | 1
Sub Total Carried to Summary
3 | Supplying, installing, testing and commissioning of direct driven PROPELLER FANS for exhaust air as shown in drawings. Each fan shall be complete with permanent split capacitor or shaded pole motor, mounting plate, accessories like wire guard, bird screen and fixed louvers for weather protection as required. Fan selection arrangement and Electrical characteristics shall be as follows :
3.1 | 450 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | No. | 4
3.2 | 375 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | No. | 4
3.3 | 300 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | No. | RO
| Sub Total Carried to Summary |  |  |  |  | 0
4 | VRV Panel
Incoming
i. | 400A. MCCB TPN 35 kA , with microprocessor release with O/C, S/C & E/F protection.
0 - 500 volts 96 x 96 sq mm digital voltmeter with switch.
1 Set
ii. | 0 - 400 Amp 96 x 96 sq mm digital ammeter with 400/5 amp CT's and selector switch.
1 Set
iii. | Phase indicating lamps, with toggle switches.
1 Set
Bus Bar
vii. | TPN bus bars shall be of aluminium and shall be sleeved. Phase bus bars shall be rated at 160 amps and neutral bus bar shall be of 50% capacity.
Outgoing
viii. | 14 Nos. 63 amps MCCB, 12.5 KW . Each of these compartment shall contain CT operated digital ammeter of 0-40 amps range with selector switch, and an indicating lamp with MCB and toggle switch for ‘ON/ OFF' status of VRV.
x. | 2 Nos. 63 amps TPN MCCB (Spare).
| VRV Panel as described above. | Set | 1
5 | CONTROL PANELS FOR FANS
Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the electrical contractor.
All outgoing shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System.
All internal wiring, power cabling and copper earthing of motors from the panel to the motor shall be included.
a. | The panel shall include the following components & accessories.
b. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA.
c. | Terminal block for power distribution as required.
d. | Contactor, over load relay with built in single phasing protection.
e. | Phase indicating lights and indicating light for `ON’ status.
f. | 144 mm x 144 mm voltmeter and digital ammeter.
g. | Time delay relay for delayed automatic restart of motor.
h. | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fan only).
i. | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation.
j. | 3 Nos of Single Pole MCB's Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare.
k. | All starters shall be provided with suitable potential free contract for connections to the Building Automation System.
220 / 24 V Transformer
5.1.1 | The number of control panels shall be as follows.
5.1.2 | 25 Amp MPCB 0.75 KW with DOL Starter | No. | 11
| Sub Total Carried to Summary |  |  |  |  | 0
B. | AIR DISTRIBUTION
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of sheet metal ducts in accordance with the approved shop drawings and as required by the specifications.
Supply& F/A
1.1 | For Ducts with External SP upto 250 Pa (ESP upto 25mmWG)
Maximum Gauge Joint Type Bracing
Duct Size Spacing
| 1 -750 mm 26 C&S Connector Nil | sq.m | 1600
| 901 - 1200 mm 24 TDF Flange Nil | sq.m | 650
| 1201 - 1801 mm 22 TDF Flange Nil | sq.m | 0
| 1801 - 2100 mm 20 TDF Flange JTR or ZEE BAR | sq.m | 0
| 2101 - above 18 TDF Flange JTR or ZEE BAR | sq.m | 0
2 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve with sandwitched 25 mm thick fibreglass insulation as per the approved shop drawings. | sq.m | 15
3 | Supply, installation and testing of galvanised steel construction Louver dampers within ducts to be provided with suitable ducts lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | sq.m | 18.5
4 | Supply, installation, testing and balancing of powder coated Extruded Aluminium supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications.
4.1 | With adjustable double louvers. | sq.m | 15
4.2 | With horizontal fixed bars | sq.m | 6
5 | Supply, installation, testing and balancing of ExhaustAir Grilles without volume control dampers.
5.1 | With adjustable double louvers powder coated extruded aluminium. | sq.m | 10
6 | Supply, installation, testing and balancing of SUPPLY Air Grilles without volume control dampers.
6.1 | With adjustable double louvers powder coated extruded aluminium. | sq.m | 9
7 | Supply, installation, testing and balancing of RETURN Air Grilles without volume control dampers.
7.1 | With adjustable double louvers powder coated extruded aluminium. | sq.m | 15
8 | Supply, installation, testing and balancing of square shape ceiling diffusers with removable core & anti smudge ring & volume control dampers as per approved drawings and specifications.
8.1 | Powder coated extruded aluminium construction. | sq.m | 20
9 | Supply, installation, testing and balancing of square shape ceiling diffusers with removable core & anti smudge ring & without volume control dampers as per approved drawings and specifications.
9.1 | Powder coated extruded aluminium construction. | sq.m | 10
10 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Damper shall be with 18G GSS body and blades shall be with aluminium airfoil construction. | sq.m | 150
11 | Supply, installation, testing and balancing of inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings.
11.1 | Powder coated/Anodised extruded aluminium construction. | sq.m | 16
12 | Supply, installation, testing and commissioning of 2 position (Open / Close) motorized dampers, duct mounted, within AHU rooms for ICUs and ORs, during EXHAUST mode operation.
12.1 | Dampers | sqm | 15
12.2 | Actuators | Nos. | 6
13 | Supply, installation , testing and commissioning Powder Coated Extruded Aluminium Air transfer door grilles with rear side frame as per approved shop drawings. | sq.m | 10
14 | Supply, installation, testing and balancing of louvers with bird screen for exhaust air as per specifications and approved drawings. | sqm | 10
14.1 | Powder coated/Anodised extruded aluminium construction. | sqm | 10
15 | Flexible Duct of 200 dia. | RM | 75
Sub Total Carried to Summary
C. | THERMAL INSULATION
1 | Supply and installation of External Thermal insulation with protective coating on ducts as per the specifications.
1.1 | 13 mm thick nitrile rubber insulation for supply air ducts in return air path. | sq.m | 1500
1.2 | 9 mm thick nitrile rubber insulation for return air ducts. | sq.m | 150
1.3 | 13 mm thick nitrile rubber insulation for supply duct (not in RA path). | sq.m | 150
1.4 | 19 mm thick nitrile rubber insulation for supply duct with 26 G Aluminium Cladding for exposed duct. | sq.m | 100
2 | Supply and installation of acoustic lining of walls of mechanical plant room covered with fibre glass tissue paper and perforated aluminium sheet OR with Nitrile rubber with density 140 - 180 kg/m3 as per the approved shop drawings & specifications.
2.1 | 15 mm thick acoustic lining with Nitrile Rubber | Sq.m. | 100
| Sub Total Carried to Summary |  |  |  |  | 0
| Total For HVAC System : "A to C" Carried to Summary |  |  |  |  | 0
Fire Alarm System
1 | INTELLIGENT ANALOGUE ADDRESSABLE FIRE DETECTION AND ALARM SYSTEM CONTROL PANELS, MODULES, SENSORS & ALARM INITIATING DEVICES
1 | Supply, installation, testing and commissioning of following as per specifications :
1.1 | Microprocessor based intelligent and electronically addressable, modular, expandable networkable, following loops (Expendable) (each loop consist of preferably a maximum of 125 detectors &125 devices) fire alarm control panel with minimum 640 character LCD display, multiple access levels, event history file in non-volatile memory (EEPROM). The panel shall have a built-in 3 fire fighting telephone zones integraded voice command center with suitable rating amplifier for 325 speaker & 8/10 zones as indicated by the number of speakers with modules as required. The panel shall support programmable relay for controlling lifts, staircase pressurizations fans, lift shaft & lift lobby pressurization fans, toilets exhaust fans, ventilation fans at fire pump room, monitoring of fire sprinkler and fire hydrant pump controlled by powerful Boolean logic equation. The panel shall have minimum five independent hazard release circuit built-in the panel.
The panel shall have 240 volts AC power supply, automatic battery charger, 24 volts, sealed lead acid maintenance free batteries sufficient for 24 hours normal working and then be capable of operating the system for 60 minutes during emergency condition.
The panel shall be UL listed.
(Tenderer to provide interfacing connectivity (BAC Net gateway/ IP) for building management system CCTV & PA system complete as per specification.)
1.1 | 2 Loops Fire Alarm Panel | Nos. | 1
1.2 | Fault isolator module for isolating shorted, dewired and loose circuits between two successive fault with automatic resetting arrangement. | Nos. | 10
1.3 | Addressable control modules for Telephone jacks office. Elevator recall, fire damper, speakers, strobes, sounder. | Nos. | 10
1.4 | Addressable monitoring module to connect NO/NC contacts such as pressure switch, flow switches, fire pump contacts (provided by Fire fighting contractor). However testing and commissioning shall be included in the fire detection and alarm system contractor scope. | Nos. | 10
1.5 | Intelligent addressable photoelectric smoke detector including mounting base with LED etc. complete as per specification | Nos. | 160
1.6 | Intelligent and electronically addressable, rate of rise cum fixed temperature thermistor type heat detector with mounting base, LED, fixed temperature setting as per specification. | Nos. | 4
1.7 | Intelligent and electronically addressablehigh sensitivity four dimensional / laser detector with microprocessor in head and including the base with LED etc as per specification for server rooms | Nos. | RO
1.8 | Intelligent 3D multisensor detector (Model No. SIGA-PHS) and electronically addressable high sensitivity detector with microprocessor in head and including the base with LED & 0.67% to 3.77% obscuration/feet etc as per specification for server rooms | Nos. | 1
1.9 | Addressable manual pull station as per specification | Nos. | 10
1.1 | Sounder with mutitones for easy understanding and exit. | Nos. | 10
1.11 | Hooter with signaling strobe light with 110 cd intensity as per specification | Nos. | 10
1.12 | Sounder with Strobe light with 110 CD intensity as per specification. | Nos. | 10
1.13 | Round speaker ceiling / wall mounting arrangement (0-2 watts) with multiple taping complete as per specification | Nos. | 130
1.14 | Fire Fightrers Telephone Jack as required | Nos. | 10
1.15 | Fire fighters Handset consisting of all units as required. | Sets | 10
2 | CABLES
2.1 | Supplying, installing, testing and commissioning of cabling for fire detection and alarm system with copper conductor PVC insulated FRLS wire of the following sizes as per specifications in existing conduit complete as required.
a. | 2 x 1.5 sq.mm. | RM | 3500
b. | 4 x 1.5 sq.mm. | RM | 100
2.2 | Supplying and laying of 2C x 1.5 sq.mm 1100 volts grade PVC insulated inner sheathed, FRLS PVC outer sheathed copper conductor armoured cable as per specification includes anchor fasters wall / ceiling with suitable clamps, saddles, fixing bolts including connecting, testing and commissioning. | RM | 200
2.3 | Supply, installation, testing and commissioning of 1 pair PVC insulated 0.61 mm. tinned copper Telephone wire as per specifications in existing conduit. | RM | 200
2.4 | Supplying, installing, testing and commissioning of single pair PVC insulated twisted shielded flexible 32 / 0.2 mm dia annealed tinned copper conductor wire in existing conduits. | RM | 3500
2.5 | Supplying, installing, testing and commissioning of following 16 gauge MS conduits recessed in RCC walls or clamped on surface in ceilings including clamps hardwares etc. complete as per specifications
a. | 20 mm dia | RM | RO
b. | 25 mm dia | RM | 3200 |  |  | 0
| TOTAL FOR FIRE ALARM SYSTEM CARRIED TO SUMMARY (1+2+3) |  |  |  |  | 0
CCTV SYSTEM
A | CLOSE CIRCUIT TELEVISION SYSTEM (COLOURED) IP SYSTEM
1 | Supply, installation, testing and commissioning of outdoor IP 36X optical and 12X digital Pan/Tilt/Zoom Day Night cameras including integrated Housing , Connectors, Lens, Camera Mounts,Power Supply including all Ancillary Equipment & accessories including Remote Reciever Unit and Pan Tilt Unit as per specification and UL Approved.
1.1 | Wall mounted | Nos. | 6
2 | Supply, installation, testing and commissioning of IP Fixed indoor 3.5 - 8 mm auto iris POE (Power on Ethernet) cameras including integrated housing (dome type), Connectors, A.I.Lens, Camera Mounts, including all Ancillary Equipment & accessories. | Nos. | 60
3 | Supply, installation, testing and commissioning of Indoor IP 18X optical and 12 X Digital Pan/Tilt/Zoom cameras including integrated Housing (dome type), Connectors, Lens, Camera Mounts,Power Supply including all Ancillary Equipment & accessories. | Nos. | R/O
4 | Supply, installation, testing and commissioning of IP digital video management system complete with server grade PC/ network video recorder for the digital video management software. The server/ recorder should include the required software for video management complete with licenses equal to the number of cameras, three client licenses, and all other licenses required to integrate keyboards, monitors etc. The system shall also include RAID backup device sufficient to store all cameras at 4CIF/D1/VGA resolution for minimum 30 Days Backups at 25fps . The system shall include all the required Network Video recorder and Viewing Software for 3 client workstations (including supply of 3 Nos. suitable PC with 19" monitor. | Lot | 1
5 | Supply, installation of 24 port Layer - 3 active switch with (POE) & number of ports as to support all cameras and having 20% spare ports, patch panel all connectors complete in all respect (minimum no. of fiber port required - 2) as per specification. | No. | RO
6 | Supply, installation of 12 port Layer - 2 active switch with (POE) with minimum 2 fiber port, with patch panel connectors with complete accessories, as per specification. | No. | RO
7 | Supply, installation, testing and commissioning of 19" rack for mounting 24 PORT 1 No. switch, 12 PORT 24 Nos switch & jack panel complete with wire manager, front tined glass door, fan, tray, power supply strip etc. | Set | RO
8 | Supply & laying of CAT 6A cable for communication in existing conduit. | RM | 4200
9 | Supply and fixing of 2mm thick heavy duty PVC conduit in following sizes including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab cutting chasis and making good or surface mounted including all fixing hardware.
9.1 | 25 mm dia | RM | 800
9.2 | 32 mm dia | RM | 1500
10 | Supply & laying of 6 core, Single mode optical fiber cable (For ethernet to ethernet) | RM | 100
| TOTAL FOR CCTV SYSTEM , NRS. |  |  |  |  | 0